MECHANICAL DESIGN MANUAL SUMMARY SHEET

SUBJECT:		Terminal Air Boxes, Diffusers, and Grilles

DESCRIPTION:	Basic Sizing Information

SPEC SECTION:	15930

APPLICABLE CODES:

N/A

DATE:		July, 1999

PREPARED BY:	Sheetmetal Committee (Ryan Hornbuckle)

Terminal air boxes should be sized so that the inlet velocity is less than 2500 fpm for noise control.  The manufacturers of the terminal boxes list a cfm for their boxes that have a much higher velocity.  In the past boxes have been sized at 2000 fpm but at minimum settings the boxes tend to have a velocity low enough that they become difficult to control.  As an example a Trane model VCWE box with reheat  has the following flow according to the catalog data:

8" dia. Inlet: 1100 cfm (listed airflow) / 0.35 sq.ft. = 3143 fpm

The same box with our sizing criteria has the following flow:

8" dia. Inlet: 870 cfm / 0.35 sq.ft. = 2486 fpm

TAB boxes should be sized using the following guidelines (Based on Trane model VCWE Terminal Air Boxes):

| Sizing Single Duct Boxes (2500 fpm) |  |  |  |
| --- | --- | --- | --- |
| TAB Inlet Size (in) | Maximum Air Flow (cfm) | Approximate Pressure Drop (in. w.g.)* | Minimum Air Flow (cfm)** |
| 6 | 490 | 0.30 | 90 |
| 8 | 870 | 0.33 | 165 |
| 10 | 1360 | 0.24 | 255 |
| 12 | 1960 | 0.25 | 360 |
| 14 | 2670 | 0.25 | 480 |
| 16 | 3490 | 0.34 | 630 |

*  	Based on maximum cfm. We usually allow up to 0.75" pressure drop an a typical box.

** 	Based on DDC controls.  Minimums are slightly higher with pneumatic controls.

| Sizing Parallel Fan Powered Boxes |  |  |  |
| --- | --- | --- | --- |
| Non-Ducted Return to Box (0.5 in. w.g.) |  | Ducted Return to Box (0.75 in. w.g.) |  |
| Fan cfm | Motor hp | Fan cfm | Motor hp |
| 75-260 | 1/15 | N/A | 1/15 |
| 250-425 | 1/8 | 50-125 | 1/8 |
| 640-1240 | 1/3 | 430-875 | 1/3 |
| 1050-1450 | 1/2 | 750-1050 | 1/2 |
| Not Listed | 3/4 | Not Listed | 3/4 |

Grilles and diffusers should be sized based on NC rating.  The acceptable NC rating in a typical office is approximately _35.  The designer should also be aware of throw, velocity, and pressure drop when selecting grilles and diffusers.

| Sizing of Typical 24x24Ceiling Diffusers (Based on T&B DML Diffusers) |  |  |
| --- | --- | --- |
| Round Inlet Size (in) | CFM Constant Volume | CFM for VAV |
| 6 | 110 | 125 |
| 8 | 250 | 300 |
| 10 | 400 | 450 |
| 12 | 600 | 650 |
| 15 | 750 | 850 |

| Sizing of Typical 24x24 Perforated Return Grilles (Based on T&B PR Grilles) |  |
| --- | --- |
| Round Inlet Size (in) | CFM |
| 6 | 100 |
| 8 | 200 |
| 10 | 300 |
| 12 | 500 |
| 14 | 800 |
| 16 | 1200 |

| Sizing of Typical Non-Ducted Perforated Return Grilles (Based on T&B PT Grilles) |  |
| --- | --- |
| Face Size (in) | CFM |
| 24x12 | 400 |
| 24x24 | 800 |

| Sizing of Typical Ducted Supply Grilles (Based on T&B T54 Grilles with 40 double deflection) |  | Sizing of Typical Ducted Return/Exhaust Grilles (Based on T&B T70D Grilles with 40 single deflection) |  |
| --- | --- | --- | --- |
| Face Size (in) | CFM | Face Size (in) | CFM |
| 6x4, 6x6 | 50 | 8x4, 6x6 | 100 |
| 12x4, 8x6 | 100 | 12x6 | 200 |
| 10x6, 8x8 | 150 | 12x8, 10x10 | 300 |
| 14x6, 10x10 | 200 | 12x12 | 500 |
| 20x6, 14x8, 12x10 | 300 | 18x12 | 700 |
| 24x6, 14x10, 12x12 | 400 | 22x10, 16x16 | 800 |
| 30x6, 18x10, 14x14 | 500 | 24x12, 18x18 | 1000 |
| 36x6, 22x10, 16x14 | 600 | 34x10, 20x20 | 1200 |
| 30x8, 24x10, 16x16 | 700 | 24x18 | 1500 |
| 30x10, 24x12, 18x16 | 800 | 22x22 | 1800 |
| 28x12, 20x16, 18x18 | 900 | 24x24 | 2000 |
| 30x12, 24x16, 20x20 | 1000 | 36x18 | 2400 |
| 36x12, 26x16, 22x22 | 1200 | 34x22, 28x28 | 2700 |
| 38x14, 30x18, 24x24 | 1400 | 36x24, 30x30 | 3200 |
| 42x16, 36x18, 26x26 | 1800 | 46x22, 32x32 | 3800 |
| 44x16, 36x20, 28x28 | 2100 | 36x30, 34x34 | 4000 |
| 48x18, 42x20, 30x30 | 2400 | 48x24, 34x34 | 4200 |
| 48x20, 40x24 | 2700 | 48x30, 38x38 | 5400 |
| 42x24, 32x32 | 3000 | 48x36, 42x42 | 6400 |
| 48x24, 34x34 | 3600 |  |  |