| I N T E R | MECHANICAL DESIGN MEMO |
| --- | --- |
| O F F I C E |  |

| To: | Mechanical Design Staff |
| --- | --- |
| Subject: | Humidity Control |
| Date: | September 4, 2001 |
| Spec. Section: | 15780 – Packaged Roof Top Units 15835 – Terminal Heat Transfer Units |
| Prepared By: | Larry Pithan |

Problem

When outdoor temperatures and humidity levels are high, we often get complaints of high building humidity.  This high indoor humidity can lead to many problems including:

- Uncomfortable building conditions.

- Condensation on cold piping, diffusers, and other surfaces.

- Mold growth inside the building.

- Sagging ceiling tile.

Discussion

There are two types of HVAC systems that historically have done a poor job of maintaining indoor humidity levels during the cooling season.  These are single zone, constant volume air handling units (typically rooftop units) and unit ventilators.

Rooftop Units – Single zone, constant volume rooftop units control space temperature by varying the discharge air temperature.  This means that, except at 100% peak load conditions, the cooling will cycle on and off as required to maintain the space temperature.

We size the cooling capacity based on maximum design load conditions, and typically tend to be a little conservative.  Then we have to select a standard unit size, which often is somewhat larger than our calculated load.  After all of this, we usually end up with a unit that has excessive cooling capacity under nearly all-operating conditions.

The space thermostat senses room temperature, which is a function of sensible heat gain in the space (windows, walls, roof, lights, equipment, people, etc).  The compressor then cycles to maintain the correct space temperature.  Normal controls for this type of system do not sense space humidity.

The problem is compounded by the introduction of outside air.  Whenever the compressor is not operating, all moisture in the outside air enters directly into the space and raises the humidity level.  As we design for higher ventilation rates, this becomes more of a problem.

During periods of lower sensible heat gain, the compressor doesn’t operate for long enough periods of time to remove all the moisture being introduced by people, outside air, and moisture migration through the building envelope.  As a result, the humidity level in the space exceeds recommended levels and causes the problems listed above.

Unit Ventilators – A unit ventilator is basically a constant volume, single zone air handling unit serving an individual room.  Again, the method of space temperature control is by varying the discharge air temperature.

Most unit ventilators use chilled water coils for air conditioning.  The units can either control space temperature by modulating the chilled water flow rate or by using a constant water flow through the coil with face-and-bypass dampers.

With either type of control, space humidity cannot be adequately controlled.  For the valve- controlled scheme, the coil does not get cold enough to condense moisture out of the air-stream.  For the face-and-bypass scheme, much of the moisture-laden air bypasses the coil and therefore is not de-humidified.

The basic problem in both of these systems is the fact that all the air is not cooled enough (down to about 55 degrees) to provide dehumidification.

Other Concerns

There are other HVAC systems that can have similar humidity control issues.  Any system that operates by cycling the cooling using a space thermostat can potentially have this problem (as opposed to a system that maintains a constant discharge air temperature).   Systems to watch include:

- Heat Pumps.

- Fan Coil Units.

- Residential Furnaces.

- Package Terminal A/C Units (PTAC).

It is very important to watch your sizing of these units and look at the latent cooling capacity.  Outside air can be a big problem with these systems.  The best option is to pre-treat the outside air delivered to these systems.

We are seeing more air-to-air heat recovery devices being used to pre-treat ventilation air on these types of systems.  In some cases, we have supplied ventilation air directly from the heat recovery unit into the space or into the terminal units.  When using heat recovery, the best option is to provide additional cooling downstream of the heat recovery device to provide further dehumidification of the air.  Otherwise, the latent energy in the outside air becomes an additional load on the room HVAC system and quite likely will result in higher space humidity levels.

# Options

There are some tricks that can be done to make these systems better:

- Reduce outside air amounts to the minimum possible while still maintaining acceptable IAQ.  This will reduce the amount of moisture brought in from outside.

- Turn units (or at least the outside air) off whenever the space is not occupied.  This will reduce the amount of moisture introduced into the space.

- Operate units by cycling the fan instead of continuous fan.  This will normally cause the compressor to run whenever the fan runs.  However, this is not a good solution on most projects because there is no continuous circulation of air.

- Install a reheat coil downstream of the cooling coil.  Provide controls to bring on cooling whenever the space humidity is too high and use the reheat coil to prevent overcooling.  Basically, this turns the unit into a dehumidifier.  Note that for this to work on unit ventilator systems you will need to have a four-pipe system and the heating coil will need to be in the re-heat position.

- Use an enthalpy heat recovery wheel to pre-condition the outside air.  This can help reduce the moisture load, especially when we are supplying high amounts of outside air.  Be sure to look at how much energy (sensible and latent) is in the pre-treated ventilation air and make sure your equipment has adequate capacity to handle this load.

Although the above measures may help the problem, they seldom provide an acceptable solution.

Our experience has shown that variable volume systems do a much better job of controlling space humidity.  With these systems, all supply air is cooled to approximately 55 degrees.  At this temperature, the air can absorb moisture from the space and maintain comfort conditions.

# Actions

We should not be using these systems for any projects that require comfortable space conditions.  If we have owners who insist on the system, we need to be on record (in writing) that humidity control will be a problem.  On all future projects, the office mechanical department supervisor will need to approve the use of constant volume, single zone air handling units or unit ventilators.

LCP/smt