| I N T E R | MECHANICAL DESIGN MEMO |
| --- | --- |
| O F F I C E |  |

| To: | Mechanical Design Staff |
| --- | --- |

| Date: | April 12, 2004 |
| --- | --- |

SUBJECT:		Water Cooled Chillers – Heat and Noise Considerations

SPEC SECTION:	15684 – Centrifugal Water Chillers

REFERENCES:	ANSI/ASHRAE Standard 15 – Safety Standard for Refrigeration Systems

PREPARED BY:	Cooling Piping Committee (Brian Winterle)

Issue

Most manufacturers have refrigerant cooled compressor motors that reject the heat internally to the chiller and do not generate heat gain to the chiller mechanical room (codes call this a machinery room).  York has an open motor that does reject heat and additional noise to the machinery room.  The following issues arise:

- How is the additional heat in the room accounted for?

- How is the sound in the room accounted for?

- How do we allow open drive chillers to fairly bid the specifications on projects while not penalizing the Owner for operating costs or increasing our construction liability?

Discussion

Since machinery rooms are typically not air-conditioned, the ventilation system must be designed to account for the additional heat gain of the open drive chiller.  Machinery rooms are not typically air conditioned since they do not require normally occupied space temperatures and humidity levels.  Therefore, providing a fan coil unit for an unconditioned space may seem to defeat the purpose of mechanically cooling if the room is still only kept at 95°F.  A supplementary fan coil unit provided by the open drive chiller manufacturer is no longer our company standard.

The amount of refrigerant charge and chiller room volume determine the amount of exhaust required per ASHRAE Standard 15.  In addition to the ASHRAE requirements, the heat gain of the room must also be calculated using a 5 or 10°F temperature rise to determine the amount of cooling required.  ASHRAE 15 or the chiller motor heat gain will dictate the quantity of airflow required.  It is the responsibility of the Engineer to determine the most stringent exhaust air requirements and specify the exhaust system capacity accordingly.

Specification and design of the exhaust system should be able to accommodate all chiller designs regardless of motor type.  Various construction issues will arise if chiller motor heat gain is not accounted for in design and then an open drive chiller is allowed in the system. The methods used by the Mechanical Contractor to account for the open drive chiller in relation to louver size with the Ventilation Contractor, the louver opening size with the General Contractor, and the increased motor disconnect, starter, and conduit with the Electrical Contractor could all be construction liabilities.  All of these would affect other trades and might result in change orders that an Owner could direct KJWW to pay.  As such, all water-cooled chiller plants need to account for open motor heat gain in the ventilation system.

Although additional ventilation capacity would be specified for internally cooled chiller motors if the ventilation is based on an open drive chiller, the overall energy consumption should not increase if the thermostat setting is close to 95°F.  Since the exhaust fans will cycle to maintain setpoint, specified fans should run less frequently with a refrigerant-cooled chiller than with an open drive chiller.  If there are concerns regarding energy consumption due to larger exhaust fans, notation of the exhaust fan capacity can be made in the shop drawing phase to reduce the size after the chiller and motor type has been submitted and approved.

Once heat gain has been addressed, the need to attenuate additional sound from the open motors must be reviewed.  Since chillers are generally noisy, the following are general guidelines for limiting noise transfer regardless of chiller design:

- Locate the chiller room as far as possible from occupied and/or noise critical areas.  Avoid locating the chiller directly adjacent to or above/below occupied spaces.  Inside the building the chiller should be located near exterior walls near the shipping/receiving area or other naturally noisy areas.  Preferably the chiller plant is in its own building away from the building and/or campus to further isolate the sound.  Consider using vibration isolators for the pumps and chillers to minimize vibration and possible associated noise.

- Review architectural drawings and recommend sand-filled and painted masonry or poured concrete walls for the mechanical room.  Review and recommend floor construction and whether a concrete base needs to be added or thickened.  Remind the Architect to note all wall penetrations to be sealed not only for sound but also for limiting the passage of refrigerant gas.  Doors with gaskets and high STC ratings should be recommended to the architect.

- Be cognizant of chiller room openings in relation to the outside of the building.  Avoid locating openings by employee patios, operable windows, courtyards, or near neighboring residential properties.  Remember the whole building and interior HVAC equipment must comply with local sound ordinances, not just outdoor equipment.  Special acoustical doors and/or louvers may be needed.

If open drive chillers are allowed in the specifications and the outdoor environment or adjacent spaces are sound sensitive, an acoustical analysis should be performed to limit the chiller to a certain sound criteria.  Some ordinances require sound criteria to be met by octave band.  Generally, we would schedule a sound performance on the drawings and require the manufacturer to meet these however they see fit.  This could include an aftermarket enclosure and/or an exhaust duct located directly over the open motor with hinged cover for access to the motor.  A hood directly over the open drive can also be detailed for sound and heat capture but will require a certain distance from the chiller to meet its U.L. listing.

Action

The following are general comments that an Engineer must account for in chiller plant design:

- Review the mechanical room location relative to sound sensitive areas and recommend a better location to the Architect if it can reduce sound transmission.  In addition, feel free to comment on an Architect’s wall construction to help eliminate sound issues in the field.  Be careful not to take on liability for the sound performance of the wall, but make general comments regarding overall construction.  Sound issues that arise in the field after construction is complete generally involve expensive solutions that can cost KJWW.

- Review the types of chillers being specified with the Owner such as the advantages and disadvantages of refrigerant versus air-cooled motors and the design and construction implications of allowing both types of chillers on the project.

- As a rule of thumb from York, open drive chillers will generate .6 tons of heat gain per 100 tons of capacity or approximately 7 cfm per ton of chiller capacity at 10°F air temperature differential.  This is based on 3.5% motor inefficiency.  Typically, chiller plants reaching 1,000 tons will require more ventilation due to heat gain than ASHRAE 15 will require.  10-15 air changes per hour is a suggested minimum ventilation rate and should be at least this rate for general air movement and heat reduction.

- When the chiller shop drawings are submitted, review the actual motor heat loss and refrigerant volume to verify design exhaust airflow is adequate per ASHRAE 15 (and the applicable mechanical code) and does not exceed design basis.

- Review submitted open drive chiller sound attenuation package and final sound power levels.

- Review the machinery room during construction observations and watch for any wall penetrations that are not properly sealed.  This will greatly affect sound transmission.