MECHANICAL DESIGN MANUAL SUMMARY SHEET

SUBJECT:		Terminal Air Boxes, Diffusers, and Grilles

DESCRIPTION:	Basic Sizing Information

SPEC SECTIONS:	15930 and 15936

APPLICABLE

REFERENCES:	Titus 2003 Product Catalog

ARI Standard 885

DATE:			April 2002 (Revised October 24, 2005)

PREPARED BY:	Ductwork Committee

# TERMINAL AIR BOXES, DIFFUSERS, AND GRILLES

Sizing terminal air boxes is a compromise between controllability and noise.    At box minimums, the air velocity can be low enough that it becomes difficult to accurately control.  When scheduling terminal air boxes, the designer should consider the building type and application to decide what noise level is acceptable for the space. The designer should check the terminal air box performance at maximum and minimum airflow rates to verify there will be no noise or controllability problems.  Generally, the box inlet velocity cannot go lower than 400-500 fpm without control inaccuracy.  Terminal air boxes should be sized for noise control so the inlet velocity is less than 2,000 fpm.  Most terminal box manufacturers catalog their boxes at inlet velocities much higher than 2,000 fpm.

The manufacturers’ listed airflow rates may have an inlet velocity higher than KJWW’s recommendations.  As an example, according to the catalog data, a Titus ESV box with reheat has the following maximum flow rate:

10" diameter inlet: 1400 cfm (listed airflow) / 0.55 sq.ft. = 2545 fpm

The same box with our sizing criteria has the following maximum flow rate:

10" diameter inlet: 1100 cfm / 0.55 sq.ft. = 2000 fpm

The NC levels below are based on 1” W.C. differential static pressure between the inlet and discharge of the terminal air box.   If the terminal air box is designed to meet specific noise requirements, verify that the terminal air box differential static pressure will not be greater than 1” W.C.  The higher the inlet static pressure, the noisier the box will be. Boxes near the air handler will have higher inlet static pressure than those at the end of the supply duct.

Below are general guidelines for TAB box sizing (based on Titus model ESV Terminal Air Boxes).  Final sizing should be project specific:

| Sizing Single Duct Boxes |  |  |  |  |
| --- | --- | --- | --- | --- |
| TAB Inlet Size (in) | Maximum Air Flow (cfm) (2000 fpm) | Approximate Pressure Drop (in. w.g.)* (Basic with 1 row coil) | Minimum Air Flow (cfm) (Based on DDC Controls) | NC at Maximum Air Flow** (Discharged/Radiated @ 1” Differential SP) |
| 4 | 175 | 0.19 | 50 | 25/27 |
| 5 | 275 | 0.15 | 70 | 22/27 |
| 6 | 400 | 0.38 | 80 | 25/28 |
| 7 | 540 | 0.38 | 105 | 25/25 |
| 8 | 700 | 0.23 | 145 | 27/27 |
| 9 | 900 | 0.25 | 175 | 22/24 |
| 10 | 1100 | 0.62* | 230 | 24/29 |
| 12 | 1600 | 0.65* | 325 | 27/30 |
| 14 | 2150 | 0.57* | 450 | 21/28 |
| 16 | 2800 | 0.64* | 580 | 23/27 |
| 24x16 | 5340 | 0.60* | 1400 | 37/49 |

*  	Based on maximum cfm. KJWW design standard is to specify 0.50" maximum air pressure drop for a typical box.  If the pressure drop exceeds the maximum allowable pressure drop, a reheat coil will be required to be installed separate of the TAB.

**	ANSI Standard S12.60-2002 limits the noise in a classroom to 35 dBA, which is roughly equivalent to NC27.  Select terminal air boxes for classrooms below this level or get approval from our client.  [Note: The values above are NC, NOT dBA and are at the space, not at the box.]

| Sizing Parallel Fan Powered Boxes* |  |
| --- | --- |
| Inlet Size | Box cfm |
| 6 | 80-500 |
| 8 | 145-700 |
| 10 | 230-1090 |
| 12 | 325-1570 |
| 14 | 450-2140 |
| 16 | 580-2800 |

* Consult manufacturers’ literature when using parallel fan powered boxes.  Performance varies depending on the operating static pressure of the fan.

# GRILLES AND DIFFUSERS

Grilles and diffusers should be sized based on throw, neck velocity, pressure drop, and NC rating.  Selection based on a good NC rating will usually provide acceptable neck velocity and pressure drop. A typical installation with less than one full diameter of perfectly straight flexible duct on the inlet could be expected to have modifiers of approximately +17 dB to account for various inlet configurations.  This means a diffuser selected at NC18 might fail to keep the room below NC35.  The acceptable NC rating in a typical office is approximately 35.  Since the catalog NC levels do not reflect “as installed” noise levels, the diffusers and grilles should be selected for around 20 NC.  KJWW recommends performing sound calculations when trying to meet specific noise requirements, such as 35 dBA for classrooms.  KJWW’s specifications limit the maximum NC to 25.

Catalog ratings of NC values are normally based on ANSI/ASHRAE Standard 70.  This standard assumes multiple diameters of straight duct entering the diffuser and also assumes a 10 dB room effect correction.  A 10 dB room effect correction means the manufacturer measures the sound power leaving the diffuser and subtracts 10 dB from each octave to estimate the sound pressure at the listener.  The result is then converted to the NC value.  The actual room effect factor depends on the room.  Tall ceilings and absorptive surfaces increase the room effect factor.  Rooms that have no soft surfaces (especially when the ceiling is hard) can have room effect factors that are 10 dB louder than what diffuser ratings are based on.

Diffuser throws should also be considered when selecting the diffuser, neck size, and layout of the diffusers.  Consider the performance of diffusers at maximum and minimum airflow rates in VAV systems and verify that dumping will not occur.  The possibility of dumping is subjective.  One could look at the minimum airflow and its velocity.  Be sure that at minimum airflows, the diffuser has enough throw so that the air does not drop directly down creating unwanted cool spots.  If you think dumping may occur, use more diffusers. Also, make sure the diffusers have enough throw at minimum airflow in heating mode to get the warm air adequately mixed into the occupied space. Too low a flow/throw with a high discharge air temperature will not allow the warm air to properly mix in the occupied space.

Slot diffusers have greater turndown ratios before dumping occurs, but are more expensive per cfm delivered.  One option for perimeter zones without radiation is to use multiple slot diffusers located approximately 5-10 feet from the exterior wall and to specify some slots to wash the exterior and the rest to blow in toward the space.  In this case, “dumping” along the exterior wall is the design goal so that heat reaches the floor; but dumping in the middle of the room is prevented.

Print cut sheets of each diffuser and grille specified for a project and include the information and selections in the project design binder.  The diffusers and grilles listed below are the most common types.  Applications may require variation from these styles and sizes, such as using a 12x12 diffuser in lieu of a 24x24.  If specific performance criteria are required, the designer should note them on the drawings.  For example, if a diffuser is required to be installed close to a wall and that direction needs to be blanked off, a note should be added to the drawings to indicate this.   Diffuser and grille performance vary among manufacturers.  The designer should spot check sensitive locations and diffuser performance such as NC levels, diffuser dumping during TAB minimums during shop drawing review.   See the design manual section for diffuser, register and grille selection criteria for more information.

The following is based on an NC of 15 to 20 (the smaller neck diffusers being a lower NC):

| Sizing of Typical 24x24 Louvered Face Diffuser (Based on Titus TMS Diffuser, CD-1 in master schedule) |  |  |
| --- | --- | --- |
| Round Inlet Size (in) | CFM | Throw (ft) (Terminal Velocity 50 fpm) |
| 6 | 150 | 7 |
| 8 | 245 | 9 |
| 10 | 410 | 13 |
| 12 | 535 | 15 |
| 14 | 695 | 17 |
| 15 | 765 | 18 |

| Sizing of Typical 24x24 Architectural Panel Face Diffuser (Based on Titus OMNI Diffuser, CD-2 in master schedule) |  |  |
| --- | --- | --- |
| Round Inlet Size (in) | CFM | Throw (ft) (Terminal Velocity 50 fpm) |
| 6 | 165 | 7 |
| 8 | 265 | 11 |
| 10 | 435 | 14 |
| 12 | 580 | 16 |
| 14 | 750 | 19 |
| 15 | 840 | 20 |

| Sizing of Typical 24x24 Ducted Perforated Return Grilles (Based on Titus PAR Grilles, RG-4 in master schedule) |  |
| --- | --- |
| Round Inlet Size (in)* | CFM |
| 6 | 155 |
| 8 | 235 |
| 10 | 325 |
| 12 | 440 |
| 14 | 525 |
| 16 | 600 |

*Grilles are available with rectangular hard duct connections that can handle higher airflow rates at a lower NC.  See manufacturers’ catalog for details.

| Sizing of Typical Non-Ducted Perforated Return Grilles (Based on Titus PXP Grilles, RG-1 & 2 in master schedule) |  |
| --- | --- |
| Face Size (in) | CFM |
| 24x12 | 500 |
| 24x24 | 1000 |

| Sizing of Typical Ducted Supply Grilles (Based on Titus 300RL Grilles with double deflection with blades in the Long Direction, assuming 22.5° blade angles, SG-1 in master schedule)* |  |  | Sizing of Typical Ducted Return/Exhaust Grilles (Based on Titus 350RL with 35° single deflection blades in the Long Direction, RG-3 in the master schedule)** |  |
| --- | --- | --- | --- | --- |
| Nominal Duct Size (in) | CFM | Throw (FT) | Nominal Duct Size (in) | CFM |
| 6x6 | 115 | 15 | 6x6 | 75 |
| 8x6 | 150 | 18 | 12x6 | 165 |
| 10x6, 8x8 | 200 | 20 | 12x8, 10x10 | 225 |
| 18x6, 12x8, 10x10 | 300 | 24 | 12x12 | 265 |
| 20x6, 12x10 | 400 | 28 | 18x12, 14x14 | 400 |
| 24x6, 18x8, 12x12 | 450 | 30 | 22x10, 16x16 | 500 |
| 30x6, 18x10, 14x14 | 575 | 35 | 24x12, 18x18 | 600 |
| 36x6, 18x12, 16x14 | 675 | 37 | 34x10, 20x20 | 775 |
| 30x8, 24x10, 16x16 | 750 | 39 | 24x20 | 900 |
| 30x10, 24x12, 18x16 | 900 | 42 | 22x22 | 950 |
| 28x12, 20x16, 18x18 | 1000 | 44 | 24x24 | 1100 |
| 30x12, 24x16, 20x20 | 1200 | 50 | 36x18 | 1200 |
| 36x12, 26x16, 22x22 | 1300 | 51 | 34x22, 28x28 | 1400 |
| 38x14, 30x18, 24x24 | 1600 | 55 | 36x24, 30x30 | 1500 |
| 42x16, 36x18, 26x26 | 1800 | 60 | 46x22, 32x32 | 1700 |
| 44x16, 36x20, 28x28 | 2000 | 65 | 36x30, 34x34 | 1900 |
| 48x18, 42x20, 30x30 | 2300 | 68 | 48x24, 36x32 | 2000 |
| 48x20, 42x24 | 2600 | 73 | 48x30, 38x38 | 2200 |
| 32x32 | 2800 | 75 | 48x36, 42x42 | 2500 |
| 48x24, 34x34 | 3000 |  | 48x42, 46x46 | 3200 |

*	Note: Specifying 45° blade adjustment adds approximately 7 to the NC value (22 to 27 total).

**	Note:  If 0° blade angle is used, airflow rates can increase.  Angled blades are more aesthetically pleasing because the occupants cannot see inside the duct.  Grille NC levels vary.  Verify specific NC levels with manufacturers’ literature.  If this type of grille is mounted above head height it should be installed upside down, or else the angled blades don’t block views into the grille.