MECHANICAL DESIGN MANUAL SUMMARY SHEET

SUBJECT:		ADA Design

DESCRIPTION:	Overview of the Americans with Disabilities Act and it’s affect on mechanical design.

SPEC SECTION:	15410

APPLICABLE CODES:	American with Disabilities Act

DATE:		March 15, 2000

PREPARED BY:	Education Committee (Beth Melton & Russ Meier)

General Information:

The Americans with Disabilities Act is a civil rights legislation that prohibits discrimination against disabled individuals.  ADA needs to be followed during the design of new buildings and the remodeling of existing structures.   (Illinois Accessibility Code is a little more stringent and is not covered.)

Not all areas/fixtures need to comply with ADA.  The project architect is responsible for directing which areas/fixtures of a building need to be meet the code.  Below are some of the ADA requirements that affect mechanical design.  Attached in Appendix A are some general reach/dimension requirements.

ADA and Mechanical Design:

- General information

  - Areas designed as ‘work areas’ (i.e.  mechanical rooms) have to be accessible only so a person can enter and leave.

  - Areas of Rescue and Assistance - Require pressurization of area designated as Area of Rescue by Separate Systems.  Areas of Rescue and Assistance are not required for monitored buildings.

  - Head Room - Walks, halls, passages shall have 80 inch minimum clearance.  If the vertical clearance of an area adjoining as accessible route is reduced to less than 80 inches, a barrier to warn blind or visually-impaired persons shall be provided (i.e. mechanical rooms).

  - Gratings - If gratings are placed in walking surfaces, then they shall have no spaces greater than ½ inch wide in one direction.  If gratings have elongated openings then they shall be placed so that the long dimension is perpendicular to the main direction of travel.

  - Clear Floor Space - A clear floor space of 30x48 inches shall be provided in front of urinals.  This space must adjoin an accessible route.  Urinal shields that do not extend beyond the front edge of the urinal rim bay be provided with 29 inch clearance between them.

  - General Reach Requirements (thermostats, light switches, electrical receptacles, etc.) - When a clear floor space is provided to allow a parallel approach, devices need to be mounted between 15 and 54 inches from floor.  When only a forward approach is maintained, devices need to be mounted between 15 and 48 inches from floor.

- Water Coolers/Drinking Fountains

  - General - Where drinking fountains are provided, at least one shall be handicapped accessible.   However, persons who can not bend to use the low fountain shall be provided with a method to get a drink.  Note: In most applications, this can be accomplished with bi-level fountains.  For some remodeled buildings, a cup dispenser located next to the fountain can be installed to meet the intent of the Act.

  - Spouts

    - Heights - Shall not be higher than 36 inches from the finished floor.

    - Location - Spouts shall provide a stream of water parallel to the front of the unit at least 4 inches high to allow the insertion of a cup under the flow.  On an accessible drinking fountain with a round or oval bowl, the spout must be positioned such that the water is within 3 inches off the front edge of the fountain.

  - Controls

    - Operation - Controls shall be operable with one hand and shall not require tight grasping, pinching or twisting of the wrist.  The force to activate controls shall be no greater than 5 lbf.

    - Location - Controls shall be front or side mounted near the front edge of the fountain.

  - Clearances

    - Cantilever Units  - Units shall have a clear knee space between the bottom of the apron and the floor of at least 27 inches high, 30 inches wide and 17-19 inches deep.  Such units also require a 9 inch toe space below the unit.

    - Free Standing Units - Units with no space below them must have at least a 30 x 48 inch area in front to allow a person in a wheelchair to make a parallel approach.

    - Protruding Objects - Objects projecting from walls with their leading edges between 27 inches and 80 inches above the finished floor shall protrude no more than 4 inches into walkways, halls and corridors.  Objects mounted at or below 27 inches above the finished floor may protrude any amount.  Free standing objects mounted on posts may overhang 12 inches maximum in the 27 to 80 inch range.  Some architects will create a recess in a corridor wall to accommodate water coolers that will not comply with this requirement.

- Water Closets

  - Mounting - Water closets shall be 17-19 inches above the finished floor measured from the top of the toilet seat.  Seat shall not be ‘sprung to return’ to a lifted position.

  - Controls

    - Operation - Flush controls shall be hand operated or automatic and shall not require tight grasping, pinching or twisting of the wrist.  The force to activate controls shall be no greater than 5 lbf.

    - Location - Controls for flush valves shall be mounted on the wide side of toilet areas no more than 44 inches above the floor.

  - Note: Can have mounting interference with grab bar.  See Figure 1 for more information.  Current plumbing material list calls for shorter flush valve.

  - Note: In cases where a bed pan washer is installed with a water closet, there is typically a interference between the grab bars and the tall flush valve installation.  See Figure 2 for more information.

- Urinals

  - Mounting - Urinals shall be stall type or wall hung with an elongated rim at a maximum of 17 inches above the finished floor.

  - Clearances - A clear floor space of 30 x 48 inches shall be provided in front of urinals.  This space must adjoin an accessible route.

  - Controls - See ‘III. Water Closets’.

- Lavatories

  - Mounting - Lavatories shall be mounted with the rim or counter surface no higher than 34 inches above the finished floor.  Provide a clearance of 29 inches above the finished floor to the bottom of the apron.  Knee and toe space shall comply with the figures shown in Appendix A.

  - Exposed Pipes and Surfaces - Hot water and drain pipes shall be insulated or otherwise configured to protect against contact.  There shall be no sharp or abrasive surfaces under the lavatories.  Note: Current plumbing material list calls for offset drain and insulated piping to meet this requirement.

  - Controls - Faucets shall be hand operated or automatic and shall not require tight grasping, pinching or twisting of the wrist.  The force to activate controls shall be no greater than 5 lbf.  Lever-operated, push-type, and electronically controlled mechanisms are acceptable.

  - Note: Single occupancy restrooms can have a mounting interference between the grab bar and lavatory back splash.  In this case the lavatory should be specified without the back splash.  See attached Figure 1 for more information.

- Bathtubs

  - Seat - An in-tub seat at the head end (opposite end of tub controls) shall be provided.  See manufacturer information for clearance requirements.

  - Controls - See ‘V. Lavatories’ for operation and attached figure for location.  When provided as a shower unit, a spray hose at least 60 inches long that can be used both as a fixed shower head and as a hand held shower shall be provided.

  - Bathtub Enclosures - Enclosures shall not obstruct controls or transfer from wheelchairs onto bathtub seats.  Tracks on the rim of the tub will not be allowed.

- Shower Stalls

  - Size and Clearances - See manufacturer information for clearance requirements.

  - Seat - Where a 60 x 30 inch roll-in shower is used, the seat is to be located on the wall adjacent to the controls.

  - Controls - See ‘VI.  Bathtubs’.  In transfer shower stalls 36 X 36 inches, all controls shall be mounted on the side opposite the seat.

  - Clear Floor Space - A clear floor space must be maintained outside the stall.  For a 36x36 shower a space of 36x48 inches is required.  For a 60x30 shower, a space of 60x36 inches is required.

  - Shower Enclosures - Enclosures shall not obstruct controls or transfer from wheelchairs onto shower seats.  If curbs are provided in shower stall 36 x 36, they shall be no higher than ½ inch from inside or outside the shower.  Curbs will not be allowed for 60 x 30 inch showers at all.

  - Note: When installing a 36X36 shower stall to an existing building, the fixture may need to be recessed in the floor to meet ½ inch curb requirement.  This can turn out to be a major structural/fire rating issue and should be discussed with those trades.  Ramps with proper slope are made for the larger shower units.

- Sinks

  - Mounting - Sinks shall be mounted with the rim or counter surface no higher than 34 inches above the finished floor.  Knee clearance shall be provided under sinks of at least 27 inches high and 30 inches wide and 19 inches deep.

  - Depth - Sinks shall be a maximum of 6 ½ inches deep.

  - Exposed Pipes and Surfaces - Hot water and drain pipes shall be insulated or otherwise configured to protect against contact.  There shall be no sharp or abrasive surfaces under the sinks.

  - Controls - Faucets shall be hand operated or automatic and shall not require tight grasping, pinching or twisting of the wrist.  The force to activate controls shall be no greater than 5 lbf.  Lever-operated, push-type, and electronically controlled mechanisms are acceptable.

APPENDIX A