- CHAPTER 18-29 
WATER SERVICE CHARGES AND PLUMBING REQUIREMENTS*

* Editor's note – Chapter 18-29, Water Service Charges and Plumbing Requirements, was added by Coun. J. 3-28-01, p. 55444, § 1.

Article 1.  Administration

18-29-101     General.

18-29-101.1     Deliberately omitted.

18-29-101.2     Scope.

18-29-101.2.1     Department of Sewers requirements.

18-29-101.2.2     Department of Water requirements.

18-29-101.3     Intent

18-29-101.4     Deliberately omitted.

18-29-102     Applicability.

18-29-102.1     General.

18-29-102.2     Existing installations.

18-29-102.3     Maintenance.

18-29-102.4     Additions, alterations or repairs.

18-29-102.5     Change in occupancy.

18-29-102.6     Deliberately omitted.

18-29-102.7     Moved buildings.

18-29-102.8     Referenced codes and standards.

18-29-102.9     Requirements not covered by chapter.

18-29-103     Deliberately omitted.

18-29-104     Deliberately omitted.

18-29-105     Approval.

18-29-105.1     Modifications.

18-29-105.2     Alternative materials, methods and equipment.

18-29-105.3     Required testing.

18-29-105.3.1     Test methods.

18-29-105.3.2     Testing agency.

18-29-105.3.3     Test reports.

18-29-105.4     Alternative engineered design.

18-29-105.4.1     Design criteria.

18-29-105.4.2     Submittal.

18-29-105.4.3     Technical data.

18-29-105.4.4     Construction documents.

18-29-105.4.5     Design approval.

18-29-105.4.6     Inspection and testing.

18-29-105.5     Material and equipment reuse.

18-29-106     Permits.

18-29-106.1     Permits.

18-29-106.2     License required.

Article 2.  Definitions

18-29-201     General.

18-29-201.1     Scope.

18-29-201.2     Interchangeability.

18-29-201.3     Terms defined in other articles.

18-29-201.4     Terms not defined.

18-29-202     General definitions.

Article 3.  General Regulations

18-29-301     General.

18-29-301.1     Scope.

18-29-301.1.1     New occupancy.

18-29-301.1.2     Age of building.

18-29-301.2     System installation.

18-29-301.3     Connections to drainage system.

18-29-301.4     Connections to water supply.

18-29-301.5     Pipe, tube and fitting sizes.

18-29-301.6     Prohibited locations.

18-29-302     Exclusion of Materials Detrimental to the Sewer System.

18-29-302.1     Detrimental or dangerous materials.

18-29-302.2     Industrial wastes.

18-29-303     Materials.

18-29-303.1     Identification.

18-29-303.2     Installation of materials.

18-29-303.3     Plastic pipe, fittings and components.

18-29-303.4     Labeling.

18-29-303.4.1     Testing.

18-29-303.4.2     Inspection and identification.

18-29-303.4.2.1     Independent.

18-29-303.4.2.2     Equipment.

18-29-303.4.2.3     Personnel.

18-29-304     Rodent-Proofing.

18-29-304.1     General.

18-29-304.2     Strainer plates.

18-29-304.3     Meter boxes.

18-29-304.4     Openings for pipes.

18-29-305     Protection of Pipes and Plumbing System Components.

18-29-305.1     Corrosion.

18-29-305.2     Breakage.

18-29-305.3     Stress and strain.

18-29-305.4     Sleeves.

18-29-305.5     Pipes through or under footings or foundation walls.

18-29-305.6     Freezing.

18-29-305.6.1     Sewer depth.

18-29-305.6.2     Water main depth.

18-29-305.7     Waterproofing of openings.

18-29-305.8     Protection against physical damage.

18-29-305.9     Protection of components of plumbing system.

18-29-306     Trenching, Excavation and Backfill.

18-29-306.1     Support of piping.

18-29-306.2     Trenching and bedding.

18-29-306.2.1     Overexcavation.

18-29-306.2.2     Rock removal.

18-29-306.2.3     Soft loadbearing materials.

18-29-306.3     Backfilling.

18-29-306.4     Tunneling.

18-29-306.5     Violations – Penalties.

18-29-307     Structural Safety.

18-29-307.1     General.

18-29-307.2     Cutting, notching or boring of holes.

18-29-307.3     Penetrations of floor-ceiling assemblies and fire-resistance-rated assemblies.

18-29-307.4     Trench location.

18-29-308     Piping Support.

18-29-308.1     General.

18-29-308.2     Deliberately omitted.

18-29-308.3     Materials.

18-29-308.4     Structural attachment.

18-29-308.5     Interval of support.

18-29-308.6     Sway bracing.

18-29-308.7     Anchorage.

18-29-308.7.1     Location.

18-29-308.8     Expansion joint fittings.

18-29-308.8.1     Vertical expansion.

18-29-308.9     Stacks.

18-29-308.10     Parallel water distribution systems.

18-29-309     Floodproofing.

18-29-309.1     General.

18-29-309.1.1     Base flood elevation.

18-29-309.2     Deliberately omitted.

18-29-310     Washroom and Toilet Room Requirements.

18-29-310.1     Ventilation.

18-29-310.2     Location of fixtures and piping.

18-29-310.3     Deliberately omitted.

18-29-310.4     Water closet compartment.

18-29-311     Toilet Facilities for Workers.

18-29-311.1     General; Workmen's temporary closets.

18-29-312     Tests and Inspections.

18-29-312.1     Required tests.

18-29-312.2     Drainage and vent water test.

18-29-312.3     Deliberately omitted.

18-29-312.4     Deliberately omitted.

18-29-312.5     Water supply system test.

18-29-312.6     Gravity sewer test.

18-29-312.7     Forced sewer test.

18-29-312.8     Storm drainage system test.

18-29-312.9     Cross connection control device inspections.

Article 4.  Fixtures, Faucets and Fixture Fittings

18-29-401     General.

18-29-401.1     Scope.

18-29-401.2     Prohibited fixtures and connections.

18-29-401.3     Water conservation.

18-29-401.4     Separate toilet room.

18-29-402     Fixture Materials.

18-29-402.1     Quality of fixtures.

18-29-402.1.1     Used fixtures.

18-29-402.2     Materials for specialty fixtures.

18-29-402.3     Sheet copper.

18-29-402.4     Sheet lead.

18-29-402.5     Fixture strainer.

18-29-402.6     Fixture overflow.

18-29-403     Minimum Plumbing Facilities.

18-29-403.1     Minimum number of fixtures.

18-29-403.2     Separate facilities.

18-29-403.3     Number of occupants for both genders.

18-29-403.4     Location of employee toilet facilities in occupancies other than assembly or mercantile.

18-29-403.5     Toilet facilities in mercantile and assembly occupancies.

18-29-403.6     Customer facilities.

18-29-403.6.1     Pay facilities.

18-29-403.6.1.1     Included buildings.

18-29-403.7     Drinking fountains.

18-29-403.8     Multiple dwellings.

18-29-403.9     Kitchens.

18-29-404     Accessible Plumbing Facilities.

18-29-404.1     Where required.

18-29-405     Installation of Fixtures.

18-29-405.1     Water supply protection.

18-29-405.2     Access for cleaning.

18-29-405.2.1     Toilet room construction.

18-29-405.2.2     Day care centers.

18-29-405.3     Setting.

18-29-405.3.1     Water closets, lavatories and bidets.

18-29-405.3.2     Urinals.

18-29-405.4     Floor and wall drainage connections.

18-29-405.4.1     Floor flanges.

18-29-405.4.1.1     Hard lead floor flanges.

18-29-405.4.2     Securing floor outlet fixtures.

18-29-405.4.3     Securing wall-hung water closet bowls.

18-29-405.5     Water-tight joints.

18-29-405.6     Plumbing in mental health centers.

18-29-405.7     Design of overflows.

18-29-405.7.1     Connection of overflows.

18-29-405.8     Access to concealed connections.

18-29-406     Automatic Clothes Washers.

18-29-406.1     Approval.

18-29-406.2     Water connection.

18-29-406.3     Waste connection.

18-29-407     Bathtubs.

18-29-407.1     Approval.

18-29-407.2     Bathtub waste outlets.

18-29-407.3     Glazing.

18-29-408     Bidets.

18-29-408.1     Approval.

18-29-408.2     Water connection.

18-29-409     Dishwashing Machines.

18-29-409.1     Approval.

18-29-409.2     Water connection.

18-29-409.2.1     Water supply connection.

18-29-409.2.2     Hot water.

18-29-409.3     Waste connection.

18-29-409.3.1     Commercial dishwashers.

18-29-410     Drinking Fountains.

18-29-410.1     Approval.

18-29-410.2     Prohibited location.

18-29-411     Emergency Showers and Eyewash Stations.

18-29-411.1     Water connection.

18-29-411.2     Waste connection.

18-29-412     Floor Drains.

18-29-412.1     Approval.

18-29-412.2     Floor drain trap and strainer.

18-29-412.3     Size of floor drains.

18-29-412.4     Required location and construction.

18-29-412.4.1     Underground floor drains.

18-29-412.4.2     Sanitary waste drain.

18-29-412.4.3     Masonry or concrete floor.

18-29-412.4.4     Hospitals and nursing homes.

18-29-412.4.5     Public laundries and multiple- family dwellings.

18-29-412.4.6     Size.

18-29-412.4.7     Accessibility.

18-29-412.4.8     Provision for evaporation.

18-29-412.4.9     Floor drains in food establishments.

18-29-413     Food Waste Grinder Units.

18-29-413.1     Approval.

18-29-413.2     Domestic food waste grinder waste outlets.

18-29-413.3     Commercial food waste grinder waste outlets.

18-29-413.4     Water supply required.

18-29-414     Garbage Can Washers.

18-29-414.1     Water connection.

18-29-414.2     Waste connection.

18-29-415     Laundry Trays.

18-29-415.1     Approval.

18-29-415.2     Waste outlet.

18-29-416     Lavatories.

18-29-416.1     Approval.

18-29-416.2     Cultured marble lavatories.

18-29-416.3     Lavatory waste outlets.

18-29-417     Showers.

18-29-417.1     Approval.

18-29-417.2     Water supply riser.

18-29-417.3     Shower waste outlet.

18-29-417.4     Shower compartments.

18-29-417.4.1     Deliberately omitted.

18-29-417.4.2     Wall area.

18-29-417.4.3     Shower installation.

18-29-417.4.4     Water temperature safety.

18-29-417.4.5     Dimensions.

18-29-417.4.6     Materials.

18-29-417.4.7     Public or institution showers.

18-29-417.5     Shower floor or receptors.

18-29-417.5.1     Support.

18-29-417.5.2     Deliberately omitted.

18-29-417.6     Glazing.

18-29-418     Sinks.

18-29-418.1     Approval.

18-29-418.2     Sink waste outlets.

18-29-418.2.1     Facilities with no range oven.

18-29-419     Urinals.

18-29-419.1     Approval.

18-29-419.2     Substitution for water closets.

18-29-419.3     Urinals for public or employee toilet facilities.

18-29-419.4     Surrounding material.

18-29-420     Water Closets.

18-29-420.1     Approval.

18-29-420.2     Water closets for public or employee toilet facilities.

18-29-420.3     Water closet seats.

18-29-420.4     Water closet connections.

18-29-420.5     Deliberately omitted.

18-29-420.6     Chemical closets.

18-29-420.7     Temporary toilet facilities.

18-29-421     Whirlpool Bathtubs.

18-29-421.1     Approval.

18-29-421.2     Installation.

18-29-421.3     Drain.

18-29-421.4     Suction fittings.

18-29-422     Health Care Fixtures and Equipment.

18-29-422.1     Scope.

18-29-422.2     Deliberately omitted.

18-29-422.3     Deliberately omitted.

18-29-422.4     Deliberately omitted.

18-29-422.5     Deliberately omitted.

18-29-422.6     Deliberately omitted.

18-29-422.7     Deliberately omitted.

18-29-422.8     Deliberately omitted.

18-29-422.9     Sterilizer equipment requirements.

18-29-422.9.1     Sterilizer piping.

18-29-422.9.2     Steam supply.

18-29-422.9.3     Steam condensate return.

18-29-422.9.4     Condensers.

18-29-422.10     Special elevations.

18-29-423     Specialty Plumbing Fixtures.

18-29-423.1     Water connections.

18-29-423.2     Approval.

18-29-424     Faucets and Other Fixture Fittings.

18-29-424.1     Approval.

18-29-424.2     Hose spray.

18-29-424.3     Hand showers.

18-29-424.4     Shower valves.

18-29-425     Flushing Devices for Water Closets and Urinals.

18-29-425.1     Flushing devices required.

18-29-425.1.1     Separate for each fixture.

18-29-425.2     Flushometer valves and tanks.

18-29-425.3     Flush tanks.

18-29-425.3.1     Ball cocks.

18-29-425.3.2     Overflows in flush tanks.

18-29-425.3.3     Sheet copper.

18-29-425.3.4     Access required.

18-29-425.4     Flush pipes and fittings.

Article 5.  Water Heaters

18-29-501     General.

18-29-501.1     Scope.

18-29-501.2     Deliberately omitted.

18-29-501.3     Drain valves.

18-29-501.4     Location for access.

18-29-501.5     Water heater labeling.

18-29-501.6     Tankless water heaters.

18-29-501.6.1     Coils.

18-29-501.7     Pressure marking of storage tanks.

18-29-501.8     Temperature controls.

18-29-501.8.1     Instantaneous water heaters.

18-29-501.9     Heat exchangers.

18-29-502     Installation.

18-29-502.1     General.

18-29-502.2     Water heaters installed in non- private garages.

18-29-502.3     Rooms used as a plenum.

18-29-502.4     Prohibited location.

18-29-502.5     Water heaters installed in closets accessed through sleeping rooms or bathrooms.

18-29-502.6     Water heaters installed in attics, basements or other areas.

18-29-503     Connections.

18-29-503.1     Cold water line valve.

18-29-503.1.1     Shutoff valves.

18-29-503.2     Deliberately omitted.

18-29-504     Safety Devices.

18-29-504.1     Antisiphon devices.

18-29-504.2     Vacuum relief valve.

18-29-504.3     Energy cutoff device.

18-29-504.4     Shutdown.

18-29-504.5     Relief valve.

18-29-504.5.1     Installation.

18-29-504.6     Relief valve approval.

18-29-504.7     Relief outlet waste.

18-29-504.7.1     Discharge.

18-29-504.7.2     Location.

18-29-504.7.3     Materials.

18-29-504.8     Required pan.

18-29-504.8.1     Pan size and drain.

18-29-504.8.2     Pan drain termination.

18-29-505     Insulation.

18-29-505.1     Unfired vessel insulation.

Article 6.  Water Supply and Distribution

18-29-601     General.

18-29-601.1     Scope.

18-29-601.2     Inspections and notices.

18-29-601.3     Access for inspections.

18-29-601.4     Solar energy utilization.

18-29-602     Water Required.

18-29-602.1     General.

18-29-602.1.1     Obligations of water consumers.

18-29-602.2     Potable water required.

18-29-602.3     Deliberately omitted.

18-29-602.4     Reserve water supply.

18-29-602.4.1     Installation of line valves or taps.

18-29-602.4.2     Dual meter settings.

18-29-603     Water Service.

18-29-603.1     Size of water service pipe.

18-29-603.1.1     Size and meter spreader connection.

18-29-603.1.2     Sizing of connections.

18-29-603.1.2     Increased connection required.

18-29-603.1.3     Permits to install water supply in buildings.

18-29-603.2     Separation of water service and building sewer/drain.

18-29-603.2.1     Individual trench.

18-29-603.2.2     Permanent pavement.

18-29-603.2.3     Backfill.

18-29-603.3     Metered service.

18-29-603.3.1     Authority.

18-29-603.3.2     Connection of nonmetered to metered service.

18-29-603.3.3     Licensed and bonded contractor.

18-29-603.3.4     Location.

18-29-603.3.5     Construction of meter vaults.

18-29-603.3.6     Installation of taps.

18-29-603.3.7     Plans accompany permit application.

18-29-603.3.8     Notification of wrecking buildings.

18-29-604     Design of Building Water Distribution System.

18-29-604.1     General.

18-29-604.2     System interconnection.

18-29-604.3     Water distribution system design criteria.

18-29-604.4     Maximum flow and water consumption.

18-29-604.4.1     Deliberately omitted.

18-29-604.4.2     Water closets.

18-29-604.5     Size of fixture supply.

18-29-604.5.1     Minimum size.

18-29-604.6     Variable street pressures.

18-29-604.7     Inadequate water pressure.

18-29-604.8     Water pressure reducing valve or regulator.

18-29-604.8.1     Valve design.

18-29-604.8.2     Repair and removal.

18-29-604.9     Deliberately omitted.

18-29-604.10     Size of water supply pipes.

18-29-604.10.1     Minimum sizes of branch distributing pipes for fixtures and appliances.

18-29-604.10.1.1     Demand load.

18-29-604.10.1.2     Size of piping.

18-29-604.10.1.3     Available pressure.

18-29-604.10.2     Procedures for calculating sizing.

18-29-604.11     Air chambers required.

18-29-604.11.1     Size of air chamber.

18-29-605     Materials, Joints and Connections.

18-29-605.1     Water compatibility.

18-29-605.2     Soil and ground water.

18-29-605.3     Lead content of water supply pipe and fittings.

18-29-605.4     Water service pipe.

18-29-605.4.1     Materials for supply pipes and fittings.

18-29-605.5     Water distribution pipe.

18-29-605.6     Fittings.

18-29-605.7     Valves.

18-29-605.8     Manufactured pipe nipples.

18-29-605.9     Prohibited joints and connections.

18-29-605.10     Deliberately omitted.

18-29-605.11     Deliberately omitted.

18-29-605.12     Brass.

18-29-605.12.1     Brazed joints.

18-29-605.12.2     Mechanical joints.

18-29-605.12.3     Threaded joints.

18-29-605.12.4     Welded joints.

18-29-605.13     Gray iron and ductile iron joints.

18-29-605.14     Copper pipe.

18-29-605.14.1     Deliberately omitted.

18-29-605.14.2     Deliberately omitted.

18-29-605.14.3     Soldered joints.

18-29-605.15     Copper tubing.

18-29-605.15.1     Brazed joints.

18-29-605.15.2     Flared joints.

18-29-605.15.3     Mechanical joints.

18-29-605.15.4     Soldered joints.

18-29-605.16     CPVC plastic.

18-29-605.16.1     Mechanical joints.

18-29-605.16.2     Solvent cementing.

18-29-605.16.3     Threaded joints.

18-29-605.17     Steel.

18-29-605.17.1     Threaded joints.

18-29-605.17.2     Mechanical joints.

18-29-605.18     Deliberately omitted.

18-29-605.19     Deliberately omitted.

18-29-605.20     Deliberately omitted.

18-29-605.21     Joints between different materials.

18-29-605.21.1     Copper or copper-alloy tubing to galvanized steel pipe.

18-29-605.22     Protection for pipes and fixtures.

18-29-605.23     Hydrants and non-freeze hydrants protection.

18-29-605.24     Water supply pipe protection.

18-29-605.25     Refrigerant condensers.

18-29-605.26     Dead-ends prohibited.

18-29-605.27     Air conditioning and refrigeration systems.

18-29-605.28     Permissible exceptions.

18-29-606     Installation of the Building Water Distribution System.

18-29-606.1     Location of full-open valves.

18-29-606.2     Location of shutoff valves.

18-29-606.3     Access to valves.

18-29-606.4     Valve identification.

18-29-606.5     Water pressure booster systems.

18-29-606.5.1     Hydropneumatic system, booster pump system, gravity tank.

18-29-606.5.1.1     Requirements.

18-29-606.5.1.1.1     Pressure relief valve.

18-29-606.5.1.1.2     Compression tank.

18-29-606.5.1.1.3     Sludge drain pipe.

18-29-606.5.1.2     Booster pump system.

18-29-606.5.1.2.1     Gravity tanks.

18-29-606.5.1.2.2     Total pressure.

18-29-606.5.1.2.3     Low pressure cutoff.

18-29-606.5.2     Surge tank for pumps.

18-29-606.5.3     Check valves required.

18-29-606.5.3.1     Approval required.

18-29-606.5.4     Equipment required for tanks receiving city water.

18-29-606.5.4.1     Sludge drain pipe.

18-29-606.5.4.2     Size.

18-29-606.5.4.3     Covers and support.

18-29-606.5.5     Recycling system for vehicle wash installations.

18-29-606.5.6     Potable water inlet control and location.

18-29-606.5.7     Tank drain pipes.

18-29-606.5.8     Prohibited location of potable supply tanks.

18-29-606.5.9     Pressure relief valve requirements.

18-29-606.5.10     Pressure relief valves for hydropneumatic tanks.

18-29-606.6     Test of distribution pipes.

18-29-607     Hot Water Supply System.

18-29-607.1     Where required.

18-29-607.1.1     Water temperature.

18-29-607.1.2     Shower compartments and shower- bath combinations.

18-29-607.1.2.1     Mixed water temperature.

18-29-607.2     Heated plumbing circulating system.

18-29-607.2.1     Return piping.

18-29-607.2.1     Piping insulation.

18-29-607.2.2     Pump operation.

18-29-607.3     Thermal expansion control.

18-29-607.3.1     Pressure reducing valve.

18-29-607.3.2     Backflow prevention device or check valve.

18-29-607.4     Hot water supply to fixtures.

18-29-607.5     Expansion joints.

18-29-607.6     Prohibited connections.

18-29-608     Protection of Potable Water Supply.

18-29-608.1     General.

18-29-608.2     Plumbing fixtures.

18-29-608.3     Water supply pipes.

18-29-608.3.1     Special equipment, water supply protection.

18-29-608.4     Deliberately omitted.

18-29-608.5     Secondary water.

18-29-608.6     Prohibited use of secondary water.

18-29-608.6.1     Private water supplies.

18-29-608.7     Stop-and-waste valves prohibited.

18-29-608.8     Identification of potable and nonpotable water.

18-29-608.9     Re-utilization prohibited.

18-29-608.10     Reuse of piping.

18-29-608.11     Painting of water tanks.

18-29-608.12     Pumps and other appliances.

18-29-608.13     Backflow protection.

18-29-608.13.1     Air gap.

18-29-608.13.2     Reduced pressure principle backflow preventers.

18-29-608.13.3     Backflow preventer with intermediate atmospheric vent.

18-29-608.13.4     Barometric loop.

18-29-608.13.5     Atmospheric-type vacuum breakers.

18-29-608.13.6     Double check-valve assemblies.

18-29-608.14     Location of backflow preventers.

18-29-608.15     Protection of potable water outlets.

18-29-608.16     Connections to the potable water system.

18-29-608.16.1     Beverage carbonator.

18-29-608.16.1.1     Backflow preventer.

18-29-608.16.2     High-pressure steam boilers.

18-29-608.16.3     Connections to automatic fire sprinkler systems and standpipe systems.

18-29-608.16.4     Fire protection equipment, risers, standpipes, tanks to be drained and flushed.

18-29-608.16.5     Fire-extinguishing equipment cross- connection.

18-29-608.16.5.1     Prohibitions.

18-29-608.16.6     Chemical or petroleum pressure vessels.

18-29-608.16.6.1     Chemical or petroleum pressure vessels.

18-29-608.16.6.2     Water flushing or cooling.

18-29-608.16.6.3     Chemical, contaminated water, or sewage lines or vessels.

18-29-608.16.7     Deliberately omitted.

18-29-608.16.8     Portable cleaning equipment.

18-29-608.16.9     Dental pump equipment.

18-29-608.17     Private water supplies.

18-29-608.17.1     Well locations.

18-29-608.17.1.1     Distances.

18-29-608.17.1.2     Direct connections.

18-29-609     Health Care Plumbing.

18-29-609.1     General.

18-29-609.1.1     Where required.

18-29-609.2     Water service.

18-29-609.3     Hot water.

18-29-609.4     Vacuum breaker installation.

18-29-609.5     Prohibited water closet and clinical sink supply.

18-29-609.6     Clinical, hydrotherapeutic and radiological equipment.

18-29-609.7     Condensate drain trap seal.

18-29-609.8     Valve leakage diverter.

18-29-610     Disinfection of Potable Water System.

18-29-610.1     Scope.

18-29-611     Water Treatment Units.

18-29-611.1     Design.

18-29-611.2     Reverse osmosis systems.

Article 7.  Sanitary Drainage

18-29-701     General.

18-29-701.1     Scope.

18-29-701.2     Sewer required.

18-29-701.3     Separate sewer connection.

18-29-701.4     Sewage treatment.

18-29-701.5     Damage to drainage system or public sewer.

18-29-701.6     Tests.

18-29-701.7     Connections.

18-29-702     Materials.

18-29-702.1     Above-ground sanitary drainage and vent pipe.

18-29-702.2     Underground building drainage and vent pipe.

18-29-702.3     Building sewer pipe.

18-29-702.4     Fittings.

18-29-702.5     Chemical waste system.

18-29-702.5.1     Glass pipe.

18-29-702.5.1.1     Padding.

18-29-702.5.1.2     Thickness.

18-29-702.5.1.3     Buried pipe.

18-29-702.6     Safe pan material and construction.

18-29-702.6.1     Material.

18-29-702.6.2     Construction.

18-29-703     Building Sewer.

18-29-703.1     Building sewer pipe near the water service.

18-29-703.2     Drainage pipe in filled ground.

18-29-703.3     Sanitary and storm sewers.

18-29-703.3.1     Combined sewers.

18-29-703.4     Existing building sewers and drains.

18-29-703.4.1     Inspection of existing underground building sewers for drain and reuse.

18-29-704     Drainage Piping and Installation.

18-29-704.1     Slope of horizontal drainage piping.

18-29-704.2     Change in size.

18-29-704.3     Connections to offsets and bases of stacks.

18-29-704.4     Future fixtures.

18-29-704.5     Dead ends.

18-29-704.5.1     Freezing.

18-29-704.5.2     Deliberately omitted.

18-29-705     Joints.

18-29-705.1     General.

18-29-705.2     Deliberately omitted.

18-29-705.3     Deliberately omitted.

18-29-705.4     Brass.

18-29-705.4.1     Brazed joints.

18-29-705.4.2     Mechanical joints.

18-29-705.4.3     Threaded joints.

18-29-705.4.4     Welded joints.

18-29-705.5     Cast iron.

18-29-705.5.1     Caulked joints.

18-29-705.5.2     Compression gasket joints.

18-29-705.5.3     Mechanical joint coupling.

18-29-705.6     Concrete joints.

18-29-705.7     Copper pipe.

18-29-705.7.1     Brazed joints.

18-29-705.7.2     Mechanical joints.

18-29-705.7.3     Soldered joints.

18-29-705.7.4     Threaded joints.

18-29-705.7.5     Welded joints.

18-29-705.8     Copper tubing.

18-29-705.8.1     Brazed joints.

18-29-705.8.2     Mechanical joints.

18-29-705.8.3     Soldered joints.

18-29-705.9     Borosilicate glass joints.

18-29-705.9.1     Caulked joints.

18-29-705.10     Steel.

18-29-705.10.1     Threaded joints.

18-29-705.10.2     Mechanical joints.

18-29-705.11     Deliberately omitted.

18-29-705.12     PVC plastic.

18-29-705.12.1     Mechanical joints.

18-29-705.12.2     Solvent cementing.

18-29-705.12.3     Threaded joints.

18-29-705.13     Vitrified clay.

18-29-705.14     Joints between different materials.

18-29-705.14.1     Copper or copper-alloy tubing to cast-iron hub pipe.

18-29-705.14.2     Copper or copper-alloy tubing to galvanized steel pipe.

18-29-705.14.3     Cast-iron pipe to galvanized steel or brass pipe.

18-29-705.14.4     Plastic pipe or tubing to other piping material.

18-29-705.14.5     Deliberately omitted.

18-29-705.14.6     Borosilicate glass to other materials.

18-29-705.15     Drainage slip joints.

18-29-705.16     Caulking ferrules.

18-29-705.17     Deliberately omitted.

18-29-706     Connections Between Drainage Piping And Fixtures.

18-29-706.1     Connections and changes in direction.

18-29-706.2     Obstructions.

18-29-706.3     Installation of fittings.

18-29-707     Prohibited Joints and Connections.

18-29-707.1     Prohibited joints.

18-29-708     Cleanouts.

18-29-708.1     Scope.

18-29-708.2     Cleanout plugs.

18-29-708.3     Where required.

18-29-708.3.1     Horizontal drains within buildings.

18-29-708.3.2     Building sewers.

18-29-708.3.3     Changes of direction.

18-29-708.3.4     Base of stack.

18-29-708.3.5     Building drain and building sewer junction.

18-29-708.3.6     Manholes.

18-29-708.4     Concealed piping.

18-29-708.5     Opening direction.

18-29-708.6     Prohibited installation.

18-29-708.7     Minimum size.

18-29-708.8     Pipes 8 inches and larger.

18-29-708.9     Clearances.

18-29-708.10     Access.

18-29-709     Fixture Units.

18-29-709.1     Values for fixtures.

18-29-709.2     Fixtures not listed in Table 18-29-709.1.

18-29-709.3     Values for continuous flow.

18-29-709.4     Deliberately omitted.

18-29-709.5     Values for indirect waste receptor.

18-29-710     Drainage System Sizing.

18-29-710.1     Maximum fixture unit load.

18-29-710.1.1     Maximum fixture units.

18-29-710.1.2     Minimum size.

18-29-710.1.3     Horizontal stack offsets.

18-29-710.1.4     Vertical stack offsets.

18-29-710.2     Future fixtures.

18-29-710.3     Underground drainage piping.

18-29-711     Offsets in Drainage Piping in Buildings of Five Stories or More.

18-29-711.1     Horizontal branch connections above or below vertical stack offsets.

18-29-711.1.1     Omission of vents for vertical stack offsets.

18-29-711.2     Horizontal branch connections to horizontal stack offsets.

18-29-711.3     Horizontal stack offsets.

18-29-711.3.1     Omission of vents for horizontal stack offsets.

18-29-711.3.2     Suds pressure zones.

18-29-711.3.2.1     Height.

18-29-711.3.2.2     Upstream.

18-29-711.3.2.3     Downstream.

18-29-711.4     Offsets below lowest branch.

18-29-712     Sumps and Ejectors.

18-29-712.1     Building drains below sewer.

18-29-712.2     Check and gate valve required.

18-29-712.3     Sump design.

18-29-712.3.1     Sump pump.

18-29-712.3.2     Sump pit.

18-29-712.3.3     Discharge piping.

18-29-712.3.4     Maximum effluent level.

18-29-712.3.5     Ejector connection to the drainage system.

18-29-712.4     Sewage pumps and sewage ejectors.

18-29-712.4.1     Capacity.

18-29-712.4.2     Duplex equipment required.

18-29-713     Health Care Plumbing.

18-29-713.1     Scope.

18-29-713.2     Bedpan washers and clinical sinks.

18-29-713.3     Indirect waste.

18-29-713.4     Vacuum system station.

18-29-713.5     Bottle system.

18-29-713.6     Central disposal system equipment.

18-29-713.7     Central vacuum or disposal systems.

18-29-713.7.1     Piping.

18-29-713.7.2     Velocity.

18-29-713.8     Vent connections prohibited.

18-29-713.9     Local vents and stacks for bedpan washers.

18-29-713.9.1     Multiple installations.

18-29-713.9.2     Trap required.

18-29-713.9.3     Trap seal maintenance.

18-29-713.10     Sterilizer vents and stacks.

18-29-713.10.1     Drainage.

18-29-713.11     Sterilizer vent stack sizes.

18-29-713.11.1     Bedpan steamers.

18-29-713.11.2     Boiling-type sterilizers.

18-29-713.11.3     Pressure sterilizers.

18-29-713.11.4     Pressure instrument washer sterilizer sizes.

18-29-714     Deliberately omitted.

18-29-715     Backwater Valves.

18-29-715.1     Sewage backflow.

18-29-715.2     Fixture branches.

18-29-715.3     Material.

18-29-715.4     Seal.

18-29-715.5     Diameter.

18-29-715.6     Location.

18-29-716     Flood Control.

18-29-716.1     Flood control devices.

18-29-716.2     Flood control systems.

Article 8.  Indirect/Special Waste

18-29-801     General.

18-29-801.1     Scope.

18-29-801.2     Protection.

18-29-802     Indirect Wastes.

18-29-802.1     Where required.

18-29-802.1.1     Deliberately omitted.

18-29-802.1.2     Deliberately omitted.

18-29-802.1.3     Potable clear-water waste.

18-29-802.1.4     Nonpotable clear-water waste.

18-29-802.1.5     Waste piping.

18-29-802.1.6     Dishwashing machine.

18-29-802.1.7     Sinks.

18-29-802.2     Deliberately omitted.

18-29-802.3     Waste receptors.

18-29-802.3.1     Open hub waste receptors.

18-29-802.4     Standpipes.

18-29-803     Special Wastes.

18-29-803.1     Deliberately omitted.

18-29-803.2     Neutralizing device required for corrosive wastes.

18-29-803.3     System design.

18-29-803.4     Volatile wastes.

18-29-804     Materials, Joints and Connections.

18-29-804.1     General.

18-29-804.2     Acid waste piping material.

18-29-805     Waste Water Control.

18-29-805.1     Preliminary treatment.

18-29-805.1.1     Approval.

18-29-805.2     Prohibited wastes.

18-29-805.2.1     Maximum concentration.

18-29-805.2.2     Types of discharge.

18-29-805.3     Discharges of clean waters.

18-29-805.4     Manholes.

18-29-805.4.1     Use and permit.

18-29-805.5     Gauging and sampling.

18-29-805.5.1     Legal or financial obligation.

18-29-805.6     Sampling methods.

18-29-805.7     Analyses.

18-29-805.7.1     Preliminary treatment.

18-29-805.7.2     Written approval.

Article 9.  Vents

18-29-901     General.

18-29-901.1     Scope.

18-29-901.2     Trap seal protection.

18-29-901.2.1     Venting required.

18-29-901.3     Chemical waste vent system.

18-29-901.4     Use limitations.

18-29-901.5     Tests.

18-29-901.6     Protection from freezing.

18-29-902     Materials.

18-29-902.1     Vents.

18-29-902.2     Sheet copper.

18-29-902.3     Sheet lead.

18-29-903     Vent Stacks and Stack Vents.

18-29-903.1     Main vent required.

18-29-903.2     Vent stack required.

18-29-903.3     Vent termination.

18-29-903.4     Vent connection at base.

18-29-903.5     Vent headers.

18-29-904     Vent Terminals.

18-29-904.1     Roof extension.

18-29-904.2     Frost closure.

18-29-904.3     Flashings.

18-29-904.4     Prohibited use.

18-29-904.5     Location of vent terminal.

18-29-904.6     Extension through the wall.

18-29-905     Vent Connections and Grades.

18-29-905.1     Connection.

18-29-905.2     Grade.

18-29-905.3     Vent connection to drainage system.

18-29-905.4     Vertical rise of vent.

18-29-905.5     Height above fixtures.

18-29-905.6     Side inlet.

18-29-905.7     Vent for future fixtures.

18-29-906     Fixture Vents.

18-29-906.1     Distance of trap from vent.

18-29-906.2     Venting of fixture drains.

18-29-906.3     Crown vent.

18-29-907     Individual Vent.

18-29-907.1     Individual vent permitted.

18-29-908     Common Vent.

18-29-908.1     Individual vent as common vent.

18-29-908.2     Connection at the same level.

18-29-908.3     Connection of different levels.

18-29-909     Deliberately omitted.

18-29-910     Deliberately omitted.

18-29-911     Deliberately omitted.

18-29-912     Combination Drain and Vent System.

18-29-912.1     Type of fixtures.

18-29-912.2     Waste piping and trap.

18-29-912.2.1     Branches.

18-29-912.2.2     Sinks, lavatories, and other fixtures.

18-29-912.2.3     Long mains.

18-29-912.2.4     Floor drains.

18-29-912.3     Size.

18-29-913     Island Fixture Venting.

18-29-913.1     Limitation.

18-29-913.2     Vent connection.

18-29-913.3     Vent installation below the fixture flood level rim.

18-29-914     Relief Vents – Stacks of More Than 10 Branch Intervals.

18-29-914.1     Where required.

18-29-914.2     Size and connection.

18-29-915     Vents for Stack Offsets.

18-29-915.1     Vent for horizontal offset of drainage stack.

18-29-915.2     Upper section.

18-29-915.3     Lower section.

18-29-916     Vent Pipe Sizing.

18-29-916.1     Size of stack vents and vent stacks.

18-29-916.2     Other vents.

18-29-916.3     Required sizes of vents.

18-29-916.4     Multiple branch vents.

18-29-916.4.1     Multiple branch vents exceeding 40 feet.

18-29-916.5     Sump vents.

18-29-916.5.1     Sewage pumps and sewage ejectors other than pneumatic.

18-29-916.5.2     Pneumatic sewage ejectors.

18-29-917     Vents Not Required.

18-29-917.1     Not required.

18-29-918     Deliberately omitted.

Article 10.  Traps, Separators and Interceptors

18-29-1001     General.

18-29-1001.1     Scope.

18-29-1002     Trap Requirements.

18-29-1002.1     Fixture traps.

18-29-1002.1.1     Open plumbing.

18-29-1002.1.2     Traps underground.

18-29-1002.1.3     Animal facilities and barn drainage.

18-29-1002.1.4     Basement floor drains.

18-29-1002.1.5     Backwater valves.

18-29-1002.2     Design of traps.

18-29-1002.3     Prohibited traps.

18-29-1002.4     Trap seals.

18-29-1002.5     Size of fixture traps.

18-29-1002.6     Deliberately omitted.

18-29-1002.7     Trap setting and protection.

18-29-1002.8     Recess for trap connection.

18-29-1002.9     Acid-resisting traps.

18-29-1002.10     Plumbing in mental health centers.

18-29-1003     Interceptors and Separators.

18-29-1003.1     Interceptors required.

18-29-1003.1.1     Interceptors not required.

18-29-1003.2     Size, type and location to be approved.

18-29-1003.3     Grease interceptor or catch basin.

18-29-1003.3.1     Where required.

18-29-1003.3.2     Grease, fats and oils.

18-29-1003.3.3     Construction materials.

18-29-1003.3.4     Grease interceptors and discharge.

18-29-1003.3.5     Types.

18-29-1003.3.6     Grease trap capacity.

18-29-1003.3.7     Rate of flow controls.

18-29-1003.3.8     Efficiency of interceptors.

18-29-1003.4     Grease catch basins outside.

18-29-1003.4.1     Basin cover.

18-29-1003.5     Deliberately omitted.

18-29-1003.6     Volatile waste separator.

18-29-1003.6.1     Garages.

18-29-1003.7     Separation of liquids.

18-29-1003.7.1     General design requirements.

18-29-1003.7.2     Garage and service stations.

18-29-1003.8     Sand interceptors in commercial establishments.

18-29-1003.9     Laundries.

18-29-1003.10     Bottling establishments.

18-29-1003.11     Slaughterhouses.

18-29-1003.12     Venting of interceptors and separators.

18-29-1003.13     Access and maintenance of interceptors and separators.

18-29-1004     Materials, Joints and Connections.

18-29-1004.1     General.

Article 11.  Storm Drainage

18-29-1101     General.

18-29-1101.1     Scope.

18-29-1101.2     Where required.

18-29-1101.2.1     Roof drainage and downspouts.

18-29-1101.2.2     Drainage of areas and yards.

18-29-1101.2.3     Storm runoff.

18-29-1101.3     Prohibited drainage.

18-29-1101.4     Tests.

18-29-1101.5     Continuous flow.

18-29-1101.6     Fittings and connections.

18-29-1101.7     Roof design.

18-29-1101.8     Cleanouts required.

18-29-1101.9     Backwater valves.

18-29-1102     Materials.

18-29-1102.1     General.

18-29-1102.2     Inside storm drainage conductors.

18-29-1102.3     Underground building storm drain pipe.

18-29-1102.4     Building storm sewer pipe.

18-29-1102.5     Subsoil drain pipe.

18-29-1102.6     Roof drains.

18-29-1102.7     Fittings.

18-29-1103     Traps.

18-29-1103.1     Main trap.

18-29-1103.2     Material.

18-29-1103.3     Size.

18-29-1103.4     Cleanout.

18-29-1104     Conductors and Connections.

18-29-1104.1     Prohibited use.

18-29-1104.1.1     District sewer lines.

18-29-1104.2     Combining storm with sanitary drainage.

18-29-1104.2.1     Separate sewer systems.

18-29-1104.3     Floor drains.

18-29-1105     Roof Drains.

18-29-1105.1     Strainers.

18-29-1105.2     Flat decks.

18-29-1105.3     Roof drain flashing.

18-29-1105.4     Maximum area.

18-29-1106     Size of Conductors, Leaders and Storm Drains.

18-29-1106.1     General.

18-29-1106.2     Vertical conductors and leaders.

18-29-1106.3     Building storm drains and sewers.

18-29-1106.4     Vertical walls.

18-29-1106.5     Parapet wall scupper location.

18-29-1106.6     Size of roof gutters.

18-29-1107     Deliberately omitted.

18-29-1108     Combined Sanitary and Storm System.

18-29-1108.1     Size of combined drains and sewers.

18-29-1109     Values for Continuous Flow.

18-29-1109.1     Equivalent roof area.

18-29-1110     Controlled Flow Roof Drain Systems.

18-29-1110.1     General.

18-29-1110.1.1     Design.

18-29-1110.2     Control devices.

18-29-1110.3     Installation.

18-29-1110.4     Minimum number of roof drains.

18-29-1111     Sumps.

18-29-1111.1     Subsoil drains.

18-29-1111.2     Building subdrains.

18-29-1111.3     Pumping system.

18-29-1111.3.1     Pump capacity and head.

18-29-1111.3.2     Construction.

18-29-1111.3.3     Electrical.

18-29-1111.3.4     Piping.

Article 12.  Swimming Pools

18-29-1200     General.

18-29-1200.1     Scope.

18-29-1200.2     Definition – nonprivate swimming pool.

18-29-1200.3     Definition – private swimming pool.

Part I

18-29-1201     Nonprivate Swimming Pools Generally.

18-29-1201.1     Scope.

18-29-1201.2     Prohibited locations.

18-29-1201.3     Permit requirements.

18-29-1202     Construction.

18-29-1202.1     Nonprivate swimming pools.

18-29-1202.2     Recirculation inlets.

18-29-1202.3     Outlets.

18-29-1202.4     Hose connections.

18-29-1202.5     Overflow gutters.

18-29-1202.6     Equipment for removal of sediment.

18-29-1202.7     Recirculation system.

18-29-1202.7.1     Turnover of pool contents.

18-29-1202.8     Equipment required.

18-29-1202.9     Strainer required.

18-29-1202.10     Disinfection equipment.

18-29-1202.11     Chemical equipment.

18-29-1202.11.1     Coagulant solutions.

18-29-1202.12     Filtration equipment.

18-29-1202.12.1     Filter area.

18-29-1202.12.2     Underdrain system size.

18-29-1202.12.3     Filter sand depth.

18-29-1202.12.4     Loss-of-head gauges.

18-29-1202.12.5     Proper design.

18-29-1202.12.6     Pressure sand filter system provisions.

18-29-1202.12.7     Filter media other than sand.

18-29-1202.12.8     Sight glass.

18-29-1202.12.9     Filter piping arrangement.

18-29-1202.13     Make-up water.

18-29-1202.14     Sewage or waste water.

18-29-1202.15     Cleanouts.

18-29-1202.16     Accessibility.

18-29-1202.17     Hydrogen-ion concentration.

18-29-1202.18     Disinfectant residuals.

18-29-1203     Additional Facilities Required.

18-29-1203.1     Equipment room location and drainage.

18-29-1203.2     Dressing room drainage.

18-29-1203.3     Shower facilities.

18-29-1203.4     Toilet facilities.

18-29-1203.4.1     Inside dry.

18-29-1203.4.2     Inside wet.

18-29-1203.4.3     Fixtures.

18-29-1203.4.3.1     Smaller pools.

18-29-1203.4.3.2     Larger pools.

18-29-1203.4.4     Deliberately omitted.

18-29-1203.4.5     Backsiphonage.

18-29-1203.4.6     Cleaning.

18-29-1203.4.7     Splashing.

18-29-1203.4.8     Floors.

18-29-1203.4.9     Hose bibs.

18-29-1203.4.10     Discharge.

18-29-1203.5     Subsurface drainage.

18-29-1203.6     Drinking fountains.

18-29-1203.7     Bathhouse facilities at apartment pools.

18-29-1203.7.1     Where required.

18-29-1203.7.2     Outdoor pools.

18-29-1203.7.3     Indoor pools.

Part II

18-29-1204     Private Swimming Pools.

18-29-1204.1     Location.

18-29-1204.1.1     District limitations.

18-29-1204.1.2     Distance from property line.

18-29-1204.2     Permit required.

18-29-1204.3     Drawings, plans and permits.

18-29-1204.3.1     Presentation, examination and approval.

18-29-1204.3.2     Scale and dimensions of plan.

18-29-1204.3.3     Restrictions prior to issuance of permit.

18-29-1204.3.4     Deviation from plans.

18-29-1204.4     Recirculation pools.

18-29-1204.5     Materials.

18-29-1204.6     Structural design.

18-29-1204.7     Walk areas.

18-29-1204.8     Fences.

18-29-1204.9     Steps or ladders.

18-29-1204.10     Overflow gutters.

18-29-1204.11     Water supply.

18-29-1204.12     Inlets.

18-29-1204.12.1     Water recirculation system inlets.

18-29-1204.12.2     Makeup water.

18-29-1204.12.3     Water systems construction conformance.

18-29-1204.13     Outlets.

18-29-1204.13.1     Water recirculation system outlets.

18-29-1204.13.2     Drainage system.

18-29-1204.13.3     Drain water discharge.

18-29-1204.14     Recirculation system and appurtenances.

18-29-1204.14.1     Required apparatuses.

18-29-1204.14.2     Water volume turnover.

18-29-1204.14.3     Pump capacity.

18-29-1204.14.4     Backwash filter rate.

18-29-1204.14.5     Hair and lint strainer.

18-29-1204.14.6     Pressure filters.

18-29-1204.14.7     Disinfection equipment.

18-29-1204.14.8     Gaseous chlorination systems.

18-29-1204.15     Electrical installations.

18-29-1204.16     Maintenance.

18-29-1204.17     Inspection.

Article 13.  Referenced Standards

Appendix A
Procedures for Calculating the Minimum Sizing of the Water Supply System

- Article 1. Administration

- 18-29-101  General.

- 18-29-101.1  Deliberately omitted.

- 18-29-101.2  Scope.

The provisions of this article shall apply to the erection, installation, alteration, repairs, relocation, replacement, addition to, use or maintenance of plumbing systems within this jurisdiction.

- 18-29-101.2.1  Department of Sewers requirements.

Additional requirements that apply to the installation of plumbing systems, as enforced by the department of sewers, are included in Sections 2-96, 3-12, 4-332, 4-336, 5-4, 10-20, 10-28, 11-4 and 11-16 of the Municipal Code of Chicago.

- 18-29-101.2.2  Department of Water requirements.

Additional requirements that apply to the installation of plumbing systems, as enforced by the department of water, are included in Sections 2-108, 2-152, 4-332 and 11-12.

- 18-29-101.3  Intent

The purpose of this chapter is to provide minimum standards to safeguard life or limb, health, property and public welfare by regulating and controlling the design, construction, installation, quality of materials, location, operation, and maintenance or use of plumbing equipment and systems.

- 18-29-101.4  Deliberately omitted.

- 18-29-102  Applicability.

- 18-29-102.1  General.

The provisions of this chapter shall apply to all matters affecting or relating to structures, as set forth in Section 18-29-101.

Where, in any specific case, different sections of this chapter specify different materials, methods of construction or other requirements, the most restrictive shall govern.

- 18-29-102.2  Existing installations.

Plumbing systems lawfully in existence at the time of the adoption of this chapter shall be permitted to have their use and maintenance continued if the use, maintenance or repair is in accordance with the original design and no hazard to life, health or property is created by such plumbing system.

- 18-29-102.3  Maintenance.

All plumbing systems, materials and appurtenances, both existing and new, and all parts thereof shall be maintained in proper operating condition in accordance with the original design in a safe and sanitary condition. All devices or safeguards required by this chapter shall be maintained in compliance with the chapter edition under which they were installed. The owner or the owner's designated agent shall be responsible for maintenance of plumbing systems. To determine compliance with this provision, the Building Commissioner shall have the authority to require any plumbing system to be reinspected.

- 18-29-102.4  Additions, alterations or repairs.

Additions, alterations, renovations or repairs to any plumbing system shall conform to that required for a new plumbing system without requiring the entire existing plumbing system to comply with all the requirements of this chapter. Additions, alterations or repairs shall not cause an existing system to become unsafe, insanitary or overloaded.

- 18-29-102.5  Change in occupancy.

It shall be unlawful to make any change in the occupancy of any structure that will subject the structure to any special provision of this chapter without first obtaining a building permit.

- 18-29-102.6  Deliberately omitted.

- 18-29-102.7  Moved buildings.

Except as determined by Section 18-29-102.2, plumbing systems that are a part of buildings or structures moved into or within the jurisdiction shall comply with the provisions of this chapter for new installations.

- 18-29-102.8  Referenced codes and standards.

The codes and standards referenced in this chapter shall be those that are listed in the index and considered part of the requirements of this chapter to the prescribed extent of each such reference. Where the requirements of reference standards or manufacturer's installation instructions do not conform to minimum provisions of this chapter, the provisions of this chapter shall apply.

- 18-29-102.9  Requirements not covered by chapter.

Any requirements necessary for the strength, stability or proper operation of an existing or proposed plumbing system, or for the public safety, health and general welfare, not specifically covered by this chapter shall be determined by the building commissioner.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-103  Deliberately omitted.

- 18-29-104  Deliberately omitted.

- 18-29-105  Approval.

- 18-29-105.1  Modifications.

Whenever there are practical difficulties involved in carrying out the provisions of this chapter, the building commissioner shall have the authority to grant modifications for individual cases, provided the building commissioner shall first find that unique reasons make application of the strict letter of this chapter impractical and the modification is in conformity with the intent and purpose of this chapter and that such modification does not lessen health, life and fire safety and sanitation requirements.   The details of action granting modifications shall be recorded and entered in the files of the plumbing inspection department.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-105.2  Alternative materials, methods and equipment.

The provisions of this chapter are not intended to prevent the installation of any material or to prohibit any method of construction not specifically prescribed by this chapter, provided that any such alternative has been approved. An alternative material or method of construction shall be approved where the building commissioner finds that the proposed design is satisfactory and complies with the intent of the provisions of this chapter, and that the material, method or work offered is, for the purpose intended, at least the equivalent of that prescribed in this chapter in quality, strength, effectiveness, durability and safety.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-105.3  Required testing.

Whenever there is insufficient evidence of compliance with the provisions of this chapter, or evidence that a material or method does not conform to the requirements of this chapter, or in order to substantiate claims for alternate materials or methods, the building commissioner shall have the authority to require tests as evidence of compliance to be made at no expense to the jurisdiction.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-105.3.1  Test methods.

Test methods shall be as specified in this chapter, including section 18-29-303.4.1 or by other recognized test standards.  In the absence of recognized and accepted test methods, the building commissioner shall approve the testing procedures.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-105.3.2  Testing agency.

All tests shall be performed by an approved agency.

- 18-29-105.3.3  Test reports.

Reports of tests shall be retained by the building commissioner for the period required for retention of public records.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-105.4  Alternative engineered design.

The design, documentation, inspection, testing and approval of an alternative engineered design plumbing system shall comply with Sections 18-29-105.4.1 through 18-29-105.4.6.

- 18-29-105.4.1  Design criteria.

An alternative engineered design shall conform to the intent of the provisions of this chapter and shall provide an equivalent level of quality, strength, effectiveness, durability and safety. Material, equipment or components shall be designed and installed in accordance with the manufacturer's installation instructions.

- 18-29-105.4.2  Submittal.

The registered design professional shall indicate on the permit application that the plumbing system is an alternative engineered design. The permit and permanent permit records shall indicate that an alternative engineered design was part of the approved installation.

- 18-29-105.4.3  Technical data.

The registered design professional shall submit sufficient technical data to substantiate the proposed alternative engineered design and to prove that the performance meets the intent of this chapter.

- 18-29-105.4.4  Construction documents.

The registered design professional shall submit to the building commissioner two complete sets of signed and sealed construction documents for the alternative engineered design.  The construction documents shall include floor plans and a riser diagram of the work.  Where appropriate, the construction documents shall indicate the direction of flow, all pipe sizes, grade of horizontal piping, loading, and location of fixtures and appliances.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-105.4.5  Design approval.

Where the building commissioner determines that the alternative engineered design conforms to the intent of this chapter, the plumbing system shall be approved.  If the alternative engineered design is not approved, the building commissioner shall notify the registered design professional in writing, stating the reasons therefor.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-105.4.6  Inspection and testing.

The alternative engineered design shall be tested and inspected in accordance with the requirements of Sections and 18-29-312.*

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; appears that additional section(s) have been omitted.

- 18-29-105.5  Material and equipment reuse.

Materials, equipment and devices shall not be reused unless such elements have been reconditioned, tested, placed in good and proper working condition, and approved.

- 18-29-106  Permits.

- 18-29-106.1  Permits.

No permit shall be issued for the installation of plumbing except to a licensed registered plumbing contractor duly bonded with the City of Chicago. Nothing in this section prohibits a licensed structural engineer or a licensed architect from planning and designing plumbing systems. Nothing in this section prohibits the owner or lessee occupant of a single-family residence from himself planning, installing, altering or repairing the plumbing system of such residence; provided, however, that such plumbing shall comply with all plumbing laws, rules and regulations applicable thereto and shall be subject to inspection as may be therein provided; and provided further that any such owner or lessee may not employ any person other than a licensed registered plumbing contractor to assist him in such work. Nothing in this section prohibits a licensed drainlayer from installing or repairing subsoil drain pipe or a building sewer without being a licensed registered plumbing contractor, except for work involving iron pipe or iron fittings.

The approval and permit of the department of buildings shall be withheld until all permits have been issued by the departments of water or sewers or other authorized departments.

(Added Coun. J. 3-27-02, p. 82090, § 2)

- 18-29-106.2  License required.

No plumbing installed in violation of this code shall be approved by any department. Except for minor repairs, the Commissioners of Buildings and Water Management shall not approve any plumbing work unless the plumbing contractor installing such work has a plumbing license and is bonded with the City of Chicago, or unless such journeyman plumber has in effect a license, or unless each plumber's apprentice employed in such installation is registered as a plumber's apprentice, as required by Chapter 1( 4-332) of this code. Nothing in this section prohibits a licensed drainlayer from installing or repairing subsoil drain pipe or a building without being a licensed registered plumbing contractor, except for work involving iron pipe or iron fittings.

(Added Coun. J. 3-27-02, p. 82090, § 2; Amend Coun. J. 3-5-03, p. 104990, § 48)

- Article 2.  Definitions

- 18-29-201  General.

- 18-29-201.1  Scope.

Unless otherwise expressly stated, the following words and terms shall, for the purposes of this chapter, have the meanings shown in this article.

- 18-29-201.2  Interchangeability.

Words stated in the present tense include the future; words stated in masculine gender include the feminine and neuter; the singular number includes the plural and the plural the singular.

- 18-29-201.3  Terms defined in other articles.

Where terms are not defined in this article and are defined in other chapters of Titles 13 and 18, such terms shall have the meanings ascribed to them in those chapters.

- 18-29-201.4  Terms not defined.

Where terms are not defined in this article, such terms shall have ordinarily accepted meanings such as the context implies.

- 18-29-202  General definitions.

ACCEPTED ENGINEERING PRACTICE. Practice which conforms to accepted principles, tests or standards of nationally recognized technical or scientific authorities.

ACCESS (TO). That which enables a fixture, appliance or equipment to be reached by ready access or by a means that first requires the removal or movement of a panel, door or similar obstruction. See “Ready Access”.

ACCESS COVER. A removable plate, usually secured by bolts or screws, to permit access to a pipe or pipefitting for the purposes of inspection, repair or cleaning.

ADAPTER FITTING. An approved connecting device that suitably and properly joins or adjusts pipes and fittings which do not otherwise fit together.

AIR BREAK (DRAINAGE SYSTEM). A piping arrangement in which a drain from a fixture, appliance or device discharges indirectly into another fixture, receptacle or interceptor at a point above the flood level rim.

AIR GAP (DRAINAGE SYSTEM). The unobstructed vertical distance through the free atmosphere between the outlet of the waste pipe and the flood level rim of the receptacle into which the waste pipe is discharging.

AIR GAP (WATER DISTRIBUTION SYSTEM). The unobstructed vertical distance through the free atmosphere between the lowest opening from any pipe or faucet supplying water to a tank, plumbing fixture or other device and the flood level rim of the receptacle.

ALTERNATIVE ENGINEERED DESIGN. A plumbing system that performs in accordance with the intent of Articles 3 through 13 and provides an equivalent level of performance for the protection of public health, safety and welfare. The system design is not specifically regulated by Articles 3 through 13.

ANCHORS. An approved support for securing pipe, fixtures, and equipment to walls, ceilings, floors, or any other structural members. See “Supports”.

ANTIMICROBIAL. An additive or surface coating that inhibits the growth of bacteria or staphylococci.

ANTISIPHON. A term applied to valves or mechanical devices that eliminate siphonage.

APPROVED. See definition in Chapter 13-4 of the Municipal Code of Chicago.

AREA DRAIN. A receptacle designed to collect surface or storm water from an open area.

ASPIRATOR. A device supplied with fluid under positive pressure which passes through an integral orifice or constriction causing a partial vacuum. Any apparatus for producing a movement of fluid by the suction of that partial vacuum.

ATMOSPHERIC VACUUM BREAKER. A device consisting of a soft disc, reaction cup, stem guide with machined brass or other metal seat and large hooded atmospheric vent port used to prevent back siphonage.

BACKFLOW CONNECTION. Any arrangement whereby backflow is possible.

BACKFLOW PREVENTER. See “Reduced Pressure Principle Backflow Preventer”.

BACKPRESSURE. Pressure created by any means in the water distribution system, which by being in excess of the pressure in the water supply mains causes a potential backflow condition.

BACKPRESSURE, LOW HEAD. A pressure less than or equal to 4.33 psi (29.88 kPa) or the pressure exerted by a 10-foot (3048 mm) column of water.

BACKSIPHONAGE. The backflow of potentially contaminated water into potable water system as a result of the pressure in the potable water system falling below atmospheric pressure of the plumbing fixtures, pools, tanks or vats connected to the potable water distribution piping.

BACKWATER VALVE. A device or valve installed in the building drain or sewer pipe where a sewer is subject to backflow, and which prevents drainage or waste from backing into a low level or fixtures and causing a flooding condition.

BALLCOCK. A water supply valve, opened or closed by means of a float or similar device, utilized to supply water to a tank. An antisiphon ballcock contains an antisiphon device in the form of an approved air gap or vacuum breaker that is an integral part of the ballcock unit and that the position on the discharge side of the water supply control valve.

BATHROOM GROUP. A group of fixtures, including or excluding a bidet, and consisting of a water closet, lavatory, a bathtub or shower. Such fixtures are located together on the same floor level.

BATTERY OF FIXTURES. Any group of two or more similar adjacent fixtures which discharge into a common horizontal waste or soil branch.

BEDPAN STEAMER OR BOILER. A fixture utilized for scalding bedpans or urinals by direct application of steam or boiling water.

BEDPAN WASHER AND STERILIZER. A fixture designed to wash bedpans and to flush the contents into the sanitary drainage system. Included are fixtures of this type that provide for disinfecting utensils by scalding with steam or hot water.

BEDPAN WASHER HOSE. A device supplied with hot and cold water and located adjacent to a water closet or clinical sink to be utilized for cleansing bedpans.

BRANCH. Any part of the piping system except a riser, main or stack.

BRANCH INTERVAL. A distance along a soil or waste stack corresponding in general to a story height, but not less than 8 feet (2438 mm), within which the horizontal branches from one floor or story of a structure are connected to the stack.

BRANCH VENT. A vent connecting one or more individual vents with a vent stack or stack vent.

BUILDING. Any structure occupied or intended for supporting or sheltering any occupancy.

BUILDING DRAIN (or HOUSE DRAIN). That part of the lowest piping of a drainage system that received the discharge from soil, waste or other drainage pipes inside and that extends 60 inches (1524 mm) beyond the walls of the building and conveys the drainage to the building sewer.

Combined. A building drain that conveys both sewage and storm water or other drainage.

Sanitary. A building drain that conveys sewage only.

Storm. A building drain that conveys storm water or other drainage, but not sewage.

BUILDING SEWER (or HOUSE SEWER). That part of the drainage system that extends from the end of the building drain and conveys the discharge to a public sewer, private sewer, individual sewage disposal system or other point of disposal.

Combined. A building sewer that conveys both sewage and storm water or other drainage.

Sanitary. A building sewer that conveys sewage only.

Storm. A building sewer that conveys storm water or other drainage, but not sewage.

BUILDING SUBDRAIN. That portion of a drainage system that does not drain by gravity into the building sewer.

BUILDING TRAP. A device, fitting or assembly of fittings installed in the building drain to prevent circulation of air between the storm drainage system of the building and the building sewer.

CESSPOOL. A receptacle in the ground which receives crude sewage and is so constructed that the organic portion of such sewage is retained while the liquid portion seeps through its walls or bottom.

CHEMICAL WASTE SYSTEM. Piping which conveys corrosive or toxic chemical waste to the drainage system.

CHICAGO WATERWORKS (also WATER WORKS) SYSTEM. Includes the Chicago cribs, water purification plants, pumping stations and infrastructure necessary to deliver potable water to City of Chicago water customers.

CIRCUIT VENT. A vent that connects to a horizontal drainage branch and vents two traps to a maximum of eight traps or trapped fixtures connected into a battery.

CLEANOUT. An access opening in the drainage system utilized for the removal of obstructions. Types of cleanouts include a removable plug or cap, or a removable fixture or fixture trap.

CLEAR WATER OR CLEAR WATER WASTE. Cooling water and condensate waste from refrigeration or air condition equipment, cooled condensate from steam heating systems, and seepage water.

CLINICAL SERVICE SINK. A fixture used in healthcare occupancies used for the disposal of wastes from a bedpan or other portable waste container.

CLOSED WATER SYSTEM. If a backflow preventer device is installed in a water distribution system, that portion of the system on the outlet side of the device is considered a closed water system. A check valve or backflow preventer (e.g., a reduced pressure principle backflow preventer assembly) may be used to create a closed water system.

COMBINATION FIXTURE. A fixture combining two or more compartments or receptors.

COMBINATION WASTE AND VENT SYSTEM. A system of waste piping with the horizontal wet venting of one or more floor drains by means of a common waste and vent pipe adequately sized to provide free movement of air above the flow line of the drain.

COMBINED BUILDING DRAIN. See “Building Drain, Combined”.

COMBINED BUILDING SEWER. See “Building Sewer, Combined”.

COMMON VENT. A vent connecting at the junction of two fixture drains or to a fixture branch and serving as a vent for both fixtures.

COMMON TRAP. A trap having a water seal of not less than 2 inches (50 mm) or not more than 4 inches (100 mm).

CONCEALED FOULING SURFACE. Any surface of a plumbing fixture which is not readily visible and is not scoured or cleansed with each fixture operation.

CONDUCTOR. A pipe inside the building that conveys storm water from the roof of a storm or combined building drain.

CONNECTION. The joining of two pieces of pipe, or pipes and fittings, valves or other appurtenances.

CONTAMINATION. An impairment of the quality of the potable water that creates an actual hazard to the public health through poisoning or through the spread of disease by sewage, industrial fluids or waste.

CONTINUOUS VENT. A vertical vent that is a continuation of the drain to which it connects. The drain may be either vertical or horizontal. A continuous vent is also known as a back vent or an individual vent.

CONTINUOUS WASTE. A drain or waste line from two or more fixtures or sink compartments (of a single fixture), such as a combined three-compartment sink, connected to a single common trap.

CRITICAL LEVEL (C-L). An elevation (height) reference point that determines the minimum height at which a backflow preventer or vacuum breaker is installed above the flood level rim of the fixture or receptor served by the device. The critical level is the elevation level below which there is a potential for backflow to occur. If the critical level marking is not indicated on the device, the bottom of the device shall constitute the critical level.

CROSS CONNECTION. Any physical connection or arrangement between two otherwise separate piping systems, one of which contains potable water and the other either water of unknown or questionable safety or steam, gas or chemical, whereby there exists the possibility for flow from one system to the other, with the direction of flow depending on the pressure differential between the two systems (see “Backflow”).

Cross connection control by containment. The installation of a backflow preventer at the service connection to a premises to protect the water main.

Cross connection control by isolation. The installation of a backflow preventer at each cross connection in a premises to protect both the premises and water main.

Cross connection control (CCC). An activity designed to prevent, discover, and eliminate all cross connections.

Cross connection control device. A safety device installed in a potable water line to prevent potable water and fluids of any kind from being mixed. Cross connection control devices include, but are not limited to: atmospheric vacuum breaker, double check valve backflow preventer, double detector check valve backflow preventer, dual check valve backflow preventer, and reduced pressure principle backflow preventer.

Cross connection control device inspector. A plumber who holds an Illinois or Chicago Plumbing License and who has been certified by the Illinois Environmental Protection Agency to inspect, test, maintain and repair cross connection control devices. Such certification attests to an inspector's understanding of the principles of backflow and back siphonage and the public health hazard presented by the improper installation of cross connection control devices.

DEAD END. A pipe which is terminated at a developed distance of 2 (metric equivalent) feet or more by means of a plug or other closed fitting, except piping serving as a cleanout extension to an accessible area.

DEEP SEAL. A term applied to a trap having a water seal of more than four inches.

DEPTH OF WATER SEAL. The depth of water that would have to be removed from a full trap before air could pass through the trap.

DEVELOPED LENGTH. The length of a pipeline measured along the centerline of the pipe and fittings.

DISCHARGE PIPE. A pipe that conveys the discharges from plumbing fixtures or appliances.

DOWNSPOUT. A leader or conductor pipe which carries water from the roof or gutter to the ground or to any part of the drainage system.

DRAIN. Any pipe that carries waste water or waterborne wastes in a building drainage system.

DRAINAGE. A reversal of flow in the drainage system.

DRAINAGE FITTINGS. Special fittings utilized in the drainage system. Drainage fittings are similar to cast-iron fittings, except that instead of having a bell and spigot, drainage fittings are recessed and tapped to eliminate ridges on the inside of the installed pipe.

DRAINAGE FIXTURE UNIT. A measure of the probable discharge into the drainage system by various types of plumbing fixtures. The drainage fixture-unit valve for a particular fixture depends on its volume rate of drainage discharge, on the time duration of a single drainage operation and on the average time between successive operations.

DRAINAGE SYSTEM. All of the piping within public or private premises that conveys sewage, rainwater or other liquid wastes to a point of disposal. A drainage system does not include the mains of public sewer systems or a private or public sewage treatment or disposal plant.

Building gravity. A drainage system that drains by gravity into the building sewer.

Sanitary. A drainage system that carries sewage that excludes storm, surface and ground water.

Storm. A drainage system that carries rainwater, surface water, condensate, cooling water or similar liquid wastes.

DRAIN LAYING. Encompasses the laying and connection of piping from 60 inches (1575 mm) outside the foundation wall of a building to the public sewer system in the City right-of-way or easement.

EFFECTIVE OPENING. The minimum cross- sectional area at the point of water supply discharge, measured or expressed in terms of the diameter of a circle or, if the opening is not circular, the diameter of a circle of equivalent cross-sectional area. For faucets and similar fittings, the effective opening shall be measured at the smallest orifice in the fitting body or in the supply piping to the fitting.

EXISTING INSTALLATIONS. Any plumbing system regulated by this chapter that was legally installed prior to the effective date of this chapter, or for which a permit to install has been issued.

EXTRACTED MECHANICAL JOINT. A joint which is developed with a special drilling tool used to penetrate a copper pipe wall, after which two steel pins are extended from the drill. While rotating, the drill head is withdrawn from the pipe under power, raising an external collar from the hole in the pipe. The branch pipe is then brazed into the collared outlet.

FAUCET. A valve end of a water pipe by means of which water is drawn from or held within the pipe.

FIRE PROTECTION SYSTEMS AND EQUIPMENT. Includes but is not limited to risers, standpipes, tanks and compression tanks.

FIXTURE. See “Plumbing Fixture”.

FIXTURE BRANCH. A water supply soil or waste pipe serving one or more fixtures.

FIXTURE CARRIER. A device designed to support an off-the-floor plumbing fixture.

FIXTURE DRAIN. The drain from the trap of a fixture to a junction with any other drain pipe.

FIXTURE FITTING. A fitting that is attached to or accessible from a fixture and controls the volume and/or directional flow of water to, or conveys water from, that fixture.

FIXTURE SUPPLY. The water supply pipe connecting a fixture to a branch water supply pipe or directly to a main water supply pipe.

FIXTURE UNIT, WATER SUPPLY or WATER SUPPLY FIXTURE UNIT (W.S.F.U.). Fixture unit, water supply is mathematical* factor used by the plumbing industry to estimate the probable demand on the water supply system (considering the volume, duration of flow, and intervals between operations) caused by various plumbing fixtures.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “... is the mathematical....”

FLOAT VALVE. An automatic opening valve, operated by a float, used to control the water level in a vessel, tank or other container.

FLOOD CONTROL DEVICE. A mechanical device consisting of back water valve or valves, a motorized unit of sufficient capacity to overcome back water pressures and housing, the bottom of which is the invert of the sewer it serves, permitting gravity flow under normal conditions. The motorized unit lifts and ejects the contents of the house drain without overheating or failure by means of a by-pass to the outlet side of the back water valve.

FLOOD LEVEL RIM. The edge of the receptacle from which water overflows.

FLOOR DRAIN. A receptacle fitted with a strainer or grate and a trap or seal and connected to the plumbing or drainage system.

FLOW PRESSURE. The pressure in the water supply pipe near the faucet or water outlet while faucet or water outlet is wide open and flowing.

FLUSH TANK. A tank designed with a ballcock and flush valve to flush the contents of the bowl or usable portion of the fixture.

FLUSHOMETER TANK. A device integrated within an air accumulator vessel that is designed to discharge a predetermined quantity of water to fixtures for flushing purposes.

FLUSHOMETER VALVE (FLUSH VALVE). A valve attached to a pressurized water supply pipe and so designed that when activated it opens the line for direct flow into the fixture at a rate and quantity to operate the fixture properly, and then gradually closes to reseal fixture traps and avoid water hammer.

GRADE. The fall, pitch, or slope of a line of pipe in reference to a horizontal plane. In drainage, it is usually expressed as the fraction of an inch fall per foot length of pipe. This may also be expressed as a percentage.

GRAVEL BASIN. A receptacle through which roof water flows and which is designed to retain sediment.

GRAY WATER. Waste water, such as dishwater, or other waste water not containing fecal matter or urine.

GREASE INTERCEPTOR. A receptacle designed to cause separation and retention of oil or grease from liquid wastes.

GREASE TRAP. An interceptor located inside the building.

GROUP OF FIXTURES. Two or more fixtures adjacent to or near each other.

HANGERS. For supporting and securing pipe, fixtures, and equipment to walls, ceilings, floors, or any other structural member.

HORIZONTAL BRANCH DRAIN. A drainage branch pipe extending laterally from a soil or waste stack or building drain, with or without vertical sections or branches, that receives the discharge from two or more fixture drains or branches and conducts the discharge to the soil or waste stack or to the building drain.

HORIZONTAL PIPE. Any pipe or fitting that makes an angle of less than 45 degrees (0.79 rad) with the horizontal.

HOSE BIBB. A faucet to which a hose may be attached.

HOT BOX. A manufactured, heated enclosure installed above ground.

HOT WATER. Water at a temperature greater than or equal to 120°F (49°C).

HOUSE TRAP. See “Building Trap”.

HYDRANT. A valve or faucet for drawing water from a buried pipe which generally includes a stand pipe with a valve or faucet at the upper end. It usually has a threaded valve outlet to which a hose may be attached.

INDIRECT WASTE PIPE. A waste pipe that does not connect directly with the drainage system, but that discharges into the drainage system through an air break or air gap into a trap, fixture, receptor or inceptor to permit visibility of such discharge and to prevent a backflow into the pipe above the connection.

INDIVIDUAL SEWAGE DISPOSAL SYSTEM. A system for disposal of domestic sewage by means of a septic tank, cesspool or mechanical treatment, designed for utilization apart from a public sewer to serve a single establishment or building.

INDIVIDUAL VENT. A pipe installed to vent a fixture trap and connected with the vent system above the fixture served.

INDUSTRIAL WASTES. Industrial wastes are liquid wastes resulting from the processes employed in industrial and commercial establishments.

INTERCEPTOR. A device designed and installed to separate and retain for removal, by automatic or manual means, deleterious, hazardous or undesirable matter from normal wastes, while permitting normal sewage or wastes to discharge into the drainage system by gravity. Interceptors may be designed to remove gas, oil, sand, grit and grease.

JOINT. A joint is the juncture of two pipes, a pipe and a fitting, or two fittings.

Expansion. A loop, return bend or return offset that provides for the expansion and contraction in a piping system and is utilized in tall buildings or where there is a rapid change of temperature, as in power plants, steam rooms and similar occupancies.

Flexible. Any joint between two pipes that permits one pipe to be deflected or moved without movement or deflection of the other pipe.

Mechanical. See “Mechanical Joint”.

Slip. A type of joint made by means of a washer or a special type of packing compound in which one pipe is slipped into the end of an adjacent pipe.

LABELED. Equipment, devices, fixtures or materials bearing the label of an approved agency.

LEAD-FREE PIPE AND FITTINGS. Containing not more than 8.0 percent lead.

LEAD-FREE SOLDER AND FLUX. Containing not more than 0.2 percent lead.

LEADER. See “Downspout.”

LICENSED DESIGN PROFESSIONAL. See Section 13-40-020 of the Municipal Code of Chicago.

LOAD FACTOR. The percentage of the total connected fixture unit flow rate which is likely to occur at any point in the drainage system. The load factor varies with the type of occupancy, the total flow above the point being considered, and the probability of simultaneous use. Load factor represents the ratio of the probable load to the potential load.

LOOP VENT. A circuit vent which loops back to connect with a stack vent instead of a vent stack. Its use is limited to floor drains and floor outlet fixtures which depend on self.

MAIN. The principal pipe artery to which branches are connected.

MAIN VENT. The principal artery of the venting system, to which the vent branches may be connected.

MANHOLE. An opening constructed to permit a person to gain access to an enclosed space. In a sewer or any portion of the plumbing system. It* is used to eliminate restriction of flow at changes of direction or junctions and to facilitate cleaning.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct punctuation appears to be “...system, it....”

MANIFOLD. See “Plumbing Appurtenance”.

MAXIMUM DEMAND. The greatest requirement of flow of either water supply or waste discharge from the fixtures of a building, or any specific segment thereof.

MECHANICAL JOINT. A connection between pipes, fittings, or pipes and fittings which is not screwed, caulked, threaded, soldered, solvent cemented, brazed or welded. A joint in which compression is applied along the centerline of the pieces being joined. In some applications, the joint is part of a coupling, fitting or adapter.

MEDICAL GAS SYSTEM. The complete system to convey medical gases for direct patient application from central supply systems (bulk tanks, manifolds and medical air compressors) through piping networks with pressure and operating controls, alarm warning systems, and related components, and extending to station outlet valves at patient use points.

MEDICAL VACUUM SYSTEMS. A system consisting of central-vacuum-producing equipment with pressure and operating controls, shutoff valves, alarm- warning systems, gauges and a network of piping extending to and terminating with suitable station inlets at locations where patient suction may be required.

MINOR REPAIRS. The repair and maintenance of faucets and valves and the forcing out of obstructions in soil, waste, vent, and sewer pipes. It does not include the removal, replacement, installation or reinstallation of any pipe or plumbing fixture.

NEW PLUMBING or NEW WORK. Any new plumbing system or part thereof, or any addition to or alteration of an existing system.

NONPOTABLE WATER. Water that does not meet public health standards for drinking water and is not suitable for human consumption or culinary use. Any water of unknown quality is considered nonpotable (See “Potable Water”).

NUISANCE. Public nuisance as known in common law or in equity jurisprudence; whatever is dangerous to human life or detrimental to health; whatever structure or premises is not sufficiently ventilated, sewered, drained, cleaned or lighted, with respect to its intended occupancy; and whatever renders the air or human food or drink or water supply unwholesome.

OCCUPANCY. The purpose for which a building or portion thereof is utilized or occupied. See Chapter 13-56 for additional information.

OFFSET. A combination of approved bends that makes two changes in direction bringing one section of the pipe out of line but into a line parallel with the other section.

OPEN AIR. Outside the structure.

OPEN PLUMBING. Installation of plumbing so that traps and drainage pipes and their surroundings beneath fixtures are ventilated, accessible, and open to inspection. Open plumbing is also referred to as an exposed plumbing installation.

OPEN WATER SYSTEM. A water system with no check valve or backflow preventer installed in the service pipe.

PET COCK. A small faucet or valve used to drain water, steam, or air.

PIPE DIAMETER. Generally the interior pipe distance measured from the inside wall of a pipe (passing through the center of the pipe) to the opposite inside wall. Any referenced pipe diameter or pipe size shall mean the nominal size or diameter as designated by the commercial manufacturer.

PIPE INCREMENT. One pipe size change of a commercially available size.

PITCH. See “Grade”.

PLUMBING. Shall include all piping fixtures, appurtenances, and appliances for a supply of water for all purposes in and about buildings, structures and public places where persons live, work, or assemble and shall also include all piping, fixtures, appurtenances, and appliances for a sanitary drainage and related ventilating system within a building, and all piping, fixtures, appurtenances, and appliances outside a building connecting the building with the source of water supply on the premises or the main in the public way, also all piping, fixtures, appurtenances, appliances, drains, waste pipes carrying sewage from the foundation walls of a building to the public sewer or other disposal terminal, holding private or domestic sewage. Plumbing shall also include the installation, repair and maintenance work upon and in connection with such piping, fixtures, appurtenances, appliances, lawn sprinkler systems, drain or waste pipes, except minor repairs by a person upon his own premises.

PLUMBING APPLIANCE. Any one of a special class of plumbing fixtures intended to perform a special function. Included are fixtures having operation or control dependent on one or more energized components, such as motors, controls, heating elements, or pressure- or temperature-sensing elements. Such fixtures are manually adjusted or controlled by the owner or operator, or are operated automatically through one or more of the following actions; a time cycle, a temperature range, a pressure range, a measured volume or weight.

PLUMBING APPURTENANCE. A manufactured device, prefabricated assembly or an on-the-job assembly of component parts that is an adjunct to the basic piping system and plumbing fixtures. An appurtenance demands no additional water supply and does not add any discharge load to a fixture or to the drainage system.

PLUMBING FIXTURE. A receptacle or device that is either permanently or temporarily connected to the water distribution system of the premises and demands a supply of water therefrom; discharges waste water, liquid-borne waste materials or sewage either directly or indirectly to the drainage system of the premises; or requires both a water supply connection and a discharge to the drainage system of the premises.

PLUMBING SYSTEM. Includes the water supply and distribution pipes; plumbing fixtures and traps; water-treating or water-using equipment; soil, waste and vent pipes; and sanitary and storm sewers and building drains, in addition to their respective connections, devices and appurtenances within a structure or premises.

POP-UP WASTE. A pop-up waste consists of a waste outlet into which a sliding metal or plastic stopper is fitted, and the stopper can be raised to drain the waste. A common pop-up waste used for lavatories has a lever which passes out the side of the drain fitting and connects to a lift rod that extends on top of the lavatory or sink. The rod is lifted to lower the stopper, or depressed to raise the stopper and drain the lavatory.

POTABLE WATER. Water used for human consumption – including but not limited to water used for drinking, bathing, washing dishes, preparing foods and for watering gardens in which produce intended for human consumption is grown – which meets Safe Drinking Water Act.

PREMISES. The word “premises” wherever used in this chapter, shall be held to include a lot, or part of a lot, a building, or part of a building or any parcel or tract of land whatever.

PRESSURE GRADIENT MONITOR. A device used to protect the quality of water, failsafe by design, securing the potable water system by isolating a heat exchanger when the pressure between the potable water and the heat exchange medium drops below a preset level.

PRIVATE. In the classification of plumbing fixtures, “private” applies to fixtures in residences, condominiums and apartments, and to fixtures in nonpublic toilet rooms of hotels and motels and similar installations in buildings where the plumbing fixtures are intended for utilization by a family or an individual.

PRIVATE FIRE HYDRANT. A hydrant connected to a private water main and located on private property.

PRIVATE SEWER. A sewer not dedicated for public use, built in a street, alley, or granted easement.

PUBLIC or PUBLIC UTILIZATION. In the classification of plumbing fixtures, “public” applies to fixtures in general toilet rooms of schools, gymnasiums, hotels, airports, bus and railroad stations, public buildings, bars, public comfort stations, office buildings, stadiums, stores, restaurants, and other installations where a number of fixtures are installed so that their utilization is similarly unrestricted. Where access to fixtures in an office or other occupancy is restricted to employees or otherwise controlled these fixtures shall not be considered public.

PUBLIC SEWER. A sewer built by or constructed under the authority of the city in a public place such as a street or alley or in and through land for which an easement has been granted for the common use of the property abutting on such public place or easement.

PUBLIC WATER MAIN. Water mains are the pipes through which Lake Michigan water from the Chicago Waterworks Systems stations is distributed to any and all service pipes, fire hydrants, sprinkling systems.

QUARTER BEND. A quarter bend is a fitting changing direction of 90 degrees.

QUICK-CLOSING VALVE. A valve or faucet that closes automatically when released manually or that is controlled by a mechanical means for fast-action closing.

READY ACCESS. That which enables a fixture, appliance or equipment to be directly reached without requiring the removal or movement of any panel, door or similar obstruction and without the use of a portable ladder, step stool or similar device.

RECEPTOR. A receptacle which receives the discharge from an indirect waste and is directly connected to the inlet of a properly vented trap. It shall be of cast-iron, brass, lead or aluminum and shall be of such shape and capacity as to prevent splashing or flooding. The receptor outlet and trap shall not be less than 1 1/2 inches.

REDUCED PRESSURE PRINCIPLE BACKFLOW PREVENTER. A backflow prevention device consisting of two independently acting check valves, internally force-loaded to a normally closed position and separated by an intermediate chamber (or zone) in which there is an automatic relief means of venting to atmosphere, internally loaded to a normally open position between two tightly closing shutoff valves and with means for testing for tightness of the checks and opening of relief means.

RELIEF VALVE.

Pressure relief valve. A pressure-actuated valve held closed by a spring or other means and designed to relieve pressure automatically at the pressure at which such valve is set.

Temperature and pressure (T&P) relief valve. A combination valve designed to provide both temperature relief and pressure relief.

Temperature relief valve. A temperature- actuated valve designed to discharge automatically at the temperature at which such valve is set.

Vacuum relief valve. A valve which admits air to the system when the system is attempting to reduce its pressure to less than atmospheric.

RELIEF VENT. A vent whose primary function is to provide circulation of air between drainage and vent systems.

REVENT PIPE. A pipe which connects directly at or near the junction of an individual trap outlet with a waste or soil pipe underneath or back of a fixture and extends to a connection with the main or branch vent above the top of the fixture.

RIM. An unobstructed open edge of a fixture.

RISER. See “Water Pipe, Riser”.

ROOF DRAIN. A drain installed to receive water collection on the surface of a roof and to discharge such water into a leader or a conductor.

ROOF GUTTER. A receptacle either suspended from the edge of a roof or constructed as part of the roof to convey roof water to the down spout rain leader or conductor pipe.

ROUGH-IN. Parts of the plumbing system that are installed prior to the installation of fixtures. This includes drainage, water supply, vent piping and the necessary fixture supports and any fixtures that are built into the structure.

SAFE PAN. Device installed beneath piping and/or a fixture to collect and drain any leakage. Safe pans are especially important in food preparation/storage areas and sterile areas of health care facilities that have overhead, exposed drainage piping.

SANITARY SEWER. A house drain or house sewer designed and used to convey only sewage.

SECONDARY WATER. Water used for process purposes, which is fed through the potable water system and separated from it by means of a backflow preventer or break tank.

SELF-CLOSING FAUCET. A faucet containing a valve that automatically closes upon deactivation of the opening means.

SEPARATOR. See “Interceptor”.

SEPTIC TANK. A watertight reservoir or tank which receives sewage and by sedimentation and bacterial action effects a process of clarification and partial purification.

SEWAGE. Any liquid waste containing animal or vegetable matter in suspension or solution, including liquids containing chemicals in solution.

SEWAGE EJECTOR. A device for lifting sewage by entraining the sewage in a high-velocity jet of steam, air or water.

SIDE VENT. A vent connecting to the drain pipe through a fitting at an angle not greater than 45 degrees to the vertical.

SILL COCK. A type of lawn faucet. A faucet used on the outside of a building to which a garden hose may be attached.

SIZE OF PIPE OR TUBING. Pipe is generally sized according to the approximate dimension of its bore or inside diameter, whereas tubing is usually sized by measuring its outside diameter. Both are expressed in inches and fractions thereof. For purposes of this chapter, any referenced pipe or tubing size shall mean the nominal size or diameter as designated by the commercial manufacturer.

SLOPE. The fall (pitch) of a line of pipe in reference to a horizontal plane. In drainage, the slope is expressed as the fall in units vertical per units horizontal (percent) for a length of pipe.

SOIL PIPE. A pipe that conveys sewage containing fecal matter to the building drain or building sewer.

SOIL OR WASTE VENT. That part of the main, soil or waste pipe which extends above the highest installed branch or fixture connection.

SPILL-PROOF VACUUM BREAKER. An assembly consisting of one check valve force-loaded closed and an air-inlet vent valve forced-loaded open to atmosphere, positioned downstream of the check valve, and located between and including two tightly closing shutoff valves and a test cock.

SPECIAL WASTE. Wastes which require special handling and treatment before they may be discharged into the plumbing system.

SPECIAL WASTE PIPE. Piping which conveys special waste. Piping that has been designed and manufactured of special material to handle special waste such as acids.

STACK. A general term for any vertical line of soil, waste, vent or inside conductor piping that extends through at least one story with or without offsets.

STACK VENT. The extension of a soil or waste sack* above the highest horizontal drain connected to the stack.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “stack”.

STERILIZER.

Boiling type. A boiling-type sterilizer is a fixture of a nonpressure type utilized for boiling instruments, utensils or other equipment for disinfection. These devices are portable or are connected to the plumbing system.

Instrument. A device for the sterilization of various instruments.

Pressure (autoclave). A pressure vessel fixture designed to utilize steam under pressure for sterilizing.

Pressure Instrument Washer Sterilizer. A pressure instrument washer sterilizer is a pressure vessel fixture designed to both wash and sterilize instruments during the operating cycle of the fixture.

Utensil. A device for the sterilization of utensils as utilized in health care services.

Water. A water sterilizer is a device for sterilizing water and storing sterile water.

STERILIZER VENT. A separate pipe or stack, indirectly connected to the building drainage system at the lower terminal, that receives the vapors from nonpressure sterilizers, or the exhaust vapors from pressure sterilizers, and conducts the vapors directly to the open air. Also called vapor, steam, atmospheric or exhaust vent.

STORM DRAIN. See “Drainage System, Storm”.

SUBSOIL DRAIN. A drain that collects subsurface water or seepage water and conveys such water to a place of disposal.

SUMP. A tank or pit that receives sewage or liquid waste, located below the normal grade of the gravity system and that must be emptied by mechanical means.

SUMP PUMP. An automatic water pump powered by an electric motor for the removal of drainage, except raw sewage, from a sump, pit or low point.

SUMP VENT. A vent from pneumatic sewage ejectors, or similar equipment that terminates separately to the open air.

SUPPORTS. Devices for supporting and securing pipe, fixtures and equipment.

SWIMMING POOL. Any structure, basin chamber or tank containing an artificial body of water for swimming, diving or recreational bathing having a depth of 2 feet (610 mm) or more at any point. See Article 12.

TEMPERED WATER. Water ranging in temperature from 85°F (29°C) to 120°F (49°C).

TERMINAL. The upper portion of a soil, waste or vent pipe which project* above or through the roof of the building.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “projects”.

TEST COCK. A small cock, faucet, or valve set in a water pipe, pump, backflow device or water jacket used to drain water or test pressure.

TRAP. A fitting or device that provides a liquid seal to prevent the emission of sewer gases without materially affecting the flow of sewage or waste water through the trap.

TRAP ARM. That portion of a fixture drain between a trap and its vent.

TRAP PRIMER. A device or system of piping to maintain a water seal in a trap.

TRAP SEAL. The maximum vertical depth of liquid that a trap will retain, measured between the crown weir and the top of the dip of the trap. (CBC 13-168-020)

UNION. A coupling device used to join two pipes end-to-end, but allow them to be disconnected and reconnected. This joint can be assembled and disassembled without removing any adjacent pipes.

UNSTABLE GROUND. Earth that does not provide a uniform bearing for the barrel of the sewer pipe between the joints at the bottom of the pipe trench.

VACUUM. Any pressure less than that exerted by the atmosphere.

VACUUM BREAKER. A type of backflow preventer installed on openings subject to normal atmospheric pressure that prevents backflow by admitting atmospheric pressure through ports to the discharge side of the device.

VACUUM RELIEF VALVE. A device to prevent excessive vacuum in a pressure vessel.

VENT PIPE. “Vent pipe or vent” means any pipe provided to ventilate a plumbing system, to prevent trap siphonage and back pressure, and to equalize the air pressure within and without the piping system* the dip of the trap. See “Vent System”.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “...system at the dip....”

VENT STACK. A vertical vent pipe installed primarily for the purpose of providing circulation of air to and from any part of the drainage system and terminating to the atmosphere or in the stack vent.

VENTURI. A short section in a pipe with a reduced diameter or cross sectional area (forming a throat) compared to the larger ends, thereby increasing the velocity of the fluid passing through the throat and decreasing the pressure at the throat. This decrease in pressure allows another fluid to be drawn into the venturi.

VERTICAL PIPE. Any pipe or fitting that makes an angle of 45 degrees (0.79 rad) or more with the horizontal.

WALL-HUNG WATER CLOSET. A wall- mounted water closed* installed in such a way that the fixture does not touch the floor.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “closet”.

WASTE. The discharge from any fixture, appliance, area or appurtenance that does not contain fecal matter.

WASTE PIPE. A pipe that conveys only waste.

WATER HAMMER. The sound of concussion of moving water against the sides of a containing pipe or vessel due to a sudden flow stoppage. A pressure that results from a sudden deceleration of flow of water in a closed conduit. Also called hydraulic shock.

WATER-HAMMER ARRESTOR. A device utilized to absorb the pressure surge (water hammer) that occurs when water flow is suddenly stopped in a water supply system.

WATER HEATER. An appliance for supplying hot water for domestic commercial purposes.

WATER MAIN. A pipe or group of pipes through which Lake Michigan water from the Chicago Waterworks System pumping stations is distributed to any and all service pipes, fire hydrants and sprinkling systems.

WATER OUTLET. A discharge opening through which water is supplied to a fixture, into the atmosphere (except into an open tank that is part of the water supply system), to a boiler or heating system, or to any device or equipment requiring water to operate but which is not part of the plumbing system.

WATER PIPE.

Riser. A water supply pipe that extends one full story or more to convey water branches or to a group of fixtures.

Water distribution pipe. A pipe within the structure or on the premises that conveys water from the water service pipe, or from the meter when the meter is at the structure, to the points of utilization.

Water service pipe. The pipe from the water main or other source of potable water supply, or from the meter when the meter is at the public right of way, to the water distribution system of the building served.

WATER SUPPLY SYSTEM. The water service pipe, water distribution pipes, and the necessary connecting pipes, fittings, control valves and all appurtenances in or adjacent to the structure or premises.

WATER SUPPLY SYSTEM. The flow of water or other liquids, mixtures or substances into the distribution pipes of a potable water supply from any source except the intended source.

WATER WORKS SYSTEM. See “Chicago Waterworks”.

WELL.

Bored. A well constructed by boring a hole in the ground with an auger and installing a casing.

Drilled. A well constructed by making a hole in the ground with a drilling machine of any type and installing casing and screen.

Dug. A well constructed by excavating a large diameter shaft and installing a casing.

WHIRLPOOL BATHTUB. A plumbing appliance consisting of a bathtub fixture that is equipped and fitted with a circulating piping system designed to accept, circulate and discharge bathtub water upon each use.

YOKE VENT. A pipe connecting upward from a soil or waste stack to a vent stack for the purpose of preventing pressure changes in the stacks.

- Article 3.  General Regulations

- 18-29-301  General.

- 18-29-301.1  Scope.

The provisions of this article shall govern the general regulations regarding the installation of plumbing not specific to other articles. These provisions govern the design and installation of new plumbing or existing plumbing systems and the alteration of plumbing systems. They apply to all new construction and any remodeling or renovation that alters existing plumbing systems. These provisions do not apply to existing buildings unless the plumbing system is being altered, the building occupancy is being changed or the existing plumbing creates a health or safety hazard.

- 18-29-301.1.1  New occupancy.

If an existing building is changed from one occupancy to another it shall be treated as a new building and shall comply with the requirements of this chapter for its new occupancy.

- 18-29-301.1.2  Age of building.

Regardless of the age of the building, where a health or safety hazard exists as determined by the Building Commissioner, the owner or his agent shall install additional plumbing or make corrections as may be necessary to abate the hazard or violation of this chapter.

- 18-29-301.2  System installation.

Plumbing shall be installed with due regard to preservation of the strength of structural members, fire resistance of assemblies and prevention of damage to walls and other surfaces through fixture usage.

- 18-29-301.3  Connections to drainage system.

All plumbing fixtures, drains, appurtenances and appliances used to receive or discharge liquid wastes or sewage shall be connected properly to the drainage system of the building or premises, in accordance with the requirements of this chapter. This section shall not be construed to prevent indirect waste systems provided for in Article 8. Existing underground building sewers and drains may be reused if the pipe has been inspected by closed circuit television in the presence of a city plumbing inspector and approved for reuse by the city plumbing inspector.

- 18-29-301.4  Connections to water supply.

Every plumbing fixture, device or appliance requiring or using water for its proper operation shall be directly or indirectly connected to the water supply system in accordance with the provisions of this chapter and any rules and regulations of the department of water.

- 18-29-301.5  Pipe, tube and fitting sizes.

Unless otherwise specified, the pipe, tube and fitting sizes specified in this chapter are expressed in nominal or standard sizes as designated in the referenced material standards.

- 18-29-301.6  Prohibited locations.

Plumbing systems shall not be located in an exit stair shaft, an elevator shaft or in an elevator equipment room and other locations indicated in Titles 13-15.

Exception: Floor drains, sumps and sump pumps shall be permitted at the base of the shaft provided they are indirectly connected to the plumbing system. Refer to Chapter 18-27 for additional prohibited electrical locations.

- 18-29-302  Exclusion of Materials Detrimental to the Sewer System.

- 18-29-302.1  Detrimental or dangerous materials.

Ashes, cinders or rags; flammable, poisonous or explosive liquids or gases; oil, grease or any other insoluble material capable of obstructing, damaging or overloading the building drainage or sewer system, or capable of interfering with the normal operation of the sewage treatment processes, shall not be deposited, by any means, into such systems.

- 18-29-302.2  Industrial wastes.

Waste products from manufacturing or industrial operations shall not be introduced into the public sewer until it has been determined by the building commissioner or commissioner of water management that the introduction thereof will not damage the public sewer system or interfere with the functioning of the sewage treatment plant.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-303  Materials.

- 18-29-303.1  Identification.

The manufacturer's mark or name and the quality of the product or identification shall be cast, embossed, stamped or indelibly marked on each length of pipe and each pipe fitting, trap, fixture, material and device utilized in a plumbing system in accordance with the applicable approved standard.

- 18-29-303.2  Installation of materials.

All materials used shall be installed in strict accordance with the standards under which the materials are accepted and approved. In the absence of such installation procedures, the manufacturer's installation instructions shall be followed. Where the referenced standards or manufacturer's installation instructions do not conform to minimum provisions of this chapter, the provisions of this chapter shall apply.

- 18-29-303.3  Plastic pipe, fittings and components.

All plastic pipe, fittings and components shall be identified with the mark of an approved agency as conforming to NSF 14.

- 18-29-303.4  Labeling.

All plumbing appliances, plastic pipe, plastic fittings, plastic components, potable water pipe, potable water fittings, potable water components, faucets, fixture fittings and backflow preventers shall be labeled by an approved agency. Labeling shall be in accordance with the procedures set forth in Sections 18-29-303.4.1 through 18-29-303.4.2.3.

- 18-29-303.4.1  Testing.

An approved agency shall test a representative sample of the material or piping being labeled to the relevant standard. The approved agency shall maintain a record of all of the tests performed. The record shall provide sufficient detail to verify compliance with the test standard. The City of Chicago Department of Water Testing Lab shall be included as an approved testing lab.

- 18-29-303.4.2  Inspection and identification.

The approved agency shall periodically perform an inspection, which shall be in-plant if necessary, of the material or piping that is to be labeled. The inspection shall verify that the labeled material or piping is representative of the material or piping tested.

- 18-29-303.4.2.1  Independent.

The agency to be approved shall be objective and competent. The agency shall also disclose all possible conflicts of interest so objectivity can be confirmed.

- 18-29-303.4.2.2  Equipment.

An approved agency shall have adequate equipment to perform all required tests. The equipment shall be periodically calibrated.

- 18-29-303.4.2.3  Personnel.

An approved agency shall employ experienced personnel educated in conducting, supervising and evaluating tests.

- 18-29-304  Rodent-Proofing.

- 18-29-304.1  General.

To prevent rodents from entering structures, plumbing systems shall be designed and installed in accordance with all specifications set forth in this section.

- 18-29-304.2  Strainer plates.

All strainer plates on drain inlets shall be designed and installed so that all openings are not greater than 1/2 inch (12 mm) in least dimension.

- 18-29-304.3  Meter boxes.

Meter boxes shall be constructed in such a manner that rodents are prevented from entering a structure by way of the water service pipes connecting the meter box and structure.

- 18-29-304.4  Openings for pipes.

In or on structures where openings have been made in walls, floors or ceilings for the passage of pipes, such openings shall be closed and protected by the installation of approved metal collars that are securely fastened to adjoining structure. Openings shall have a cover consisting of concrete not less than 2 inches (50 mm) thick, heavy galvanized wire netting of 1/2 inch (12 mm) mesh, or other means for preventing passage of rodents. These requirements shall be in addition to any protection for penetrations of fire-rated assemblies required in Chapter 15-8.

- 18-29-305  Protection of Pipes and Plumbing System Components.

- 18-29-305.1  Corrosion.

Pipes passing through walls and floors made of cinder, concrete, or other corrosive material shall be protected against external corrosion by a protective sheathing or wrapping or other means that will withstand any reaction from lime and acid of concrete, cinder or other corrosive material. Sheathing or wrapping shall allow for expansion and contraction of piping to prevent any rubbing action and shall be comparable with fire stops where these are required by provisions of Titles 13 and 15. Minimum wall thickness of material shall be 0.025 inches (0.64 mm).

- 18-29-305.2  Breakage.

All pipes passing under or through walls shall be protected from breakage. All metal pipes passing through or in contact with walls and floors made of concrete or other corrosive material shall be protected against external corrosion.

- 18-29-305.3  Stress and strain.

Piping in a plumbing system shall be installed so as to prevent strains and stresses that exceed the structural strength of the pipe. Where necessary, provisions shall be made to protect piping from damage resulting from expansion, contraction and structural settlement.

- 18-29-305.4  Sleeves.

Annular spaces between sleeves and pipes shall be filled or tightly caulked in an approved manner. Annular spaces between sleeves and pipes in fire-resistance-rated assemblies shall be treated in accordance with Section 15-8-570.

- 18-29-305.5  Pipes through or under footings or foundation walls.

Any pipe that passes under a footing or through a foundation wall shall be provided with a relieving arch. Alternatively, a pipe sleeve may be built into the foundation wall. Such sleeve shall be two pipe sizes greater than the pipe passing through the wall.

- 18-29-305.6  Freezing.

A water, soil vent or waste pipe shall not be installed outside of a building, in attics or crawl spaces, nor concealed in outside walls or in any other place subjected to freezing temperature, unless adequate provision is made to protect it from freezing by insulation or heat or both. Water service pipe shall be installed not less than 60 inches (1525 mm) below grade.

- 18-29-305.6.1  Sewer depth.

The building sewers shall be installed with a minimum of 36 inches (915 mm) of cover.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-305.6.2  Water main depth.

Building water mains shall have a minimum ground cover of 60 inches (1525 mm).

- 18-29-305.7  Waterproofing of openings.

Joints at the roof around vent pipes shall be made water tight by the use of lead, copper, galvanized steel, or other approved flashing material compatible with the pipe material and roof system. Exterior wall openings shall be made water tight.

- 18-29-305.8  Protection against physical damage.

In concealed locations where piping other than cast-iron or galvanized steel is installed through holes or notches in studs, joists, rafters or similar members less than 1 1/2 inches (40 mm) from the nearest edge of the member, the pipe shall be protected by shield plates. Protective shield plates shall be a minimum of 1/16 inches (1.6 mm) thick steel, shall cover the area of the pipe where the member is notched or bored, and shall extend a minimum of 2 inches (50 mm) above sole plates and below top plates.

- 18-29-305.9  Protection of components of plumbing system.

Components of a plumbing system installed along alleyways, driveways, parking garages or other locations exposed to damage shall be recessed into the wall or otherwise protected in an approved manner.

- 18-29-306  Trenching, Excavation and Backfill.

- 18-29-306.1  Support of piping.

Buried piping shall be supported throughout its entire length.

- 18-29-306.2  Trenching and bedding.

Where trenches are excavated such that the bottom of the trench forms the bed for the pipe, solid and continuous loadbearing support shall be provided between joints. Bell holes, hub holes and coupling holes shall be provided at points where the pipe is joined. Such pipe shall not be supported on blocks to grade. In instances where the material manufacturer's installation instructions are more restrictive than those prescribed by the code, the material shall be installed in accordance with the more restrictive requirement. All such trenches and tunnels shall be kept open until the piping has been inspected, tested, and approved.

- 18-29-306.2.1  Overexcavation.

Where trenches are excavated below the installation level of the pipe such that the bottom of the trench does not form the bed for the pipe, the trench shall be backfilled to the installation level of the bottom of the pipe with sand or fine gravel placed in layers of 6 inches (150 mm) maximum depth and such backfill shall be compacted after each placement.

- 18-29-306.2.2  Rock removal.

Where rock is encountered in trenching, it shall be removed to a minimum of 3 inches (75 mm) below the installation level of the bottom of the pipe, and the trench shall be backfilled to the installation level of the bottom of the pipe with sand tamped in place so as to provide uniform loadbearing support for the pipe between joints. The pipe, including the joints, shall not rest on rock at any point.

- 18-29-306.2.3  Soft loadbearing materials.

If soft materials of poor loadbearing qualities are found at the bottom of the trench, stabilizing shall be achieved by overexcavating a minimum of two pipe diameters and backfilling to the installation level of the bottom of the pipe with fine gravel, crushed stone or a concrete foundation. The concrete foundation shall be bedded with sand tamped in place so as to provide uniform loadbearing support for the pipe between joints.

- 18-29-306.3  Backfilling.

Loose earth, free from rocks, broken concrete, frozen chunks and other rubble, shall be placed in the trench in 6-inch (150 mm) layers and tamped in place. The backfill under and beside the pipe shall be compacted for pipe support. Backfill shall be brought up evenly on both sides of the pipe so that the pipe remains aligned. Where the manufacturer's installation instructions are more restrictive than those prescribed by the code, the material shall be installed in accordance with the more restrictive requirement.

- 18-29-306.4  Tunneling.

Where pipe is to be installed by tunneling, jacking or a combination of both, the pipe shall be protected from damage during installation and from subsequent uneven loading. Where earth tunnels are used, adequate supporting structures shall be provided to prevent future settling or caving.

- 18-29-306.5  Violations – Penalties.

Any violation of Sections 18-29-306 through 18-29-306.4 shall be punished by a fine of $5,000.00 for the first offense, $5,000.00 and a 30-day suspension of a plumbing contractor's certificate of registration for the second offense, and $5,000.00 and a one-year suspension of a plumbing contractor's certificate of  registration for a third and subsequent offense.  Each day that a violation continues shall constitute a separate and distinct offense.

(Added Coun. J. 9-27-07, p. 9188, § 2)

- 18-29-307  Structural Safety.

- 18-29-307.1  General.

In the process of installing or repairing any part of a plumbing and drainage installation, the finished floors, walls, ceilings, tile work or any other part of the building or premises that must be changed or replaced shall be left in a safe structural condition and shall maintain required fire resistance in accordance with the requirements of the building code.

- 18-29-307.2  Cutting, notching or boring of holes.

A framing member shall not be cut, notched or bored in excess of limitations specified in the building code.

- 18-29-307.3  Penetrations of floor-ceiling assemblies and fire-resistance-rated assemblies.

Penetrations of floor-ceiling assemblies and assemblies required to have a fire-resistance rating shall be protected in accordance with Chapter 15-8.

- 18-29-307.4  Trench location.

Trenches installed parallel to footings shall not extend below the 45-degree (0.79 rad) bearing plane of the footing or wall.

- 18-29-308  Piping Support.

- 18-29-308.1  General.

All plumbing piping shall be supported in accordance with this section.

- 18-29-308.2  Deliberately omitted.

- 18-29-308.3  Materials.

Hangers, anchors and supports shall support the piping and the contents of the piping. Hangers and strapping material shall be of approved material that will not promote galvanic action.

- 18-29-308.4  Structural attachment.

Hangers and anchors shall be attached to the building construction in an approved manner.

- 18-29-308.5  Interval of support.

Pipe shall be supported in accordance with Table 18-29-308.5.

Table 18-29-308.5
Hanger Spacing

Piping Material; Maximum Horizontal Spacing (feet); Maximum Vertical Spacing (feet). Brass pipe; 10; 15. Cast-iron pipe a; 5; 15. Copper or copper-alloy pipe; 12; 10. Copper or copper-alloy tubing, 1 1/4-inch diameter and smaller; 6; 10. Copper or copper- alloy tubing, 1 1/2-inch diameter and larger; 10; 10. PVC pipe; 4; 4.

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm

a The maximum horizontal spacing of cast-iron pipe hangers shall be increased to 10 feet where 10-foot lengths of pipe are installed.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-308.6  Sway bracing.

Rigid support sway bracing shall be provided at changes in direction greater than 45 degrees (0.79 rad) for pipe sizes 6 inches (150 mm) and larger.

- 18-29-308.7  Anchorage.

Anchorage shall be provided to restrain drainage piping from axial movement.

- 18-29-308.7.1  Location.

For pipe sizes greater than 4 inches (100 mm), restraints shall be provided for drain pipes at all changes in direction and at all changes in diameter greater than two pipe sizes. Braces, blocks, rodding and other suitable methods as specified by coupling manufacturer shall be utilized.

- 18-29-308.8  Expansion joint fittings.

Expansion joint fittings shall be used only where necessary to provide for expansion and contraction of the pipes. Expansion joint fittings shall be of the typical material suitable for use with the type of piping in which such fittings are installed.

- 18-29-308.8.1  Vertical expansion.

In buildings more than 150 ft (45.75 m) in height, all vertical lines of piping shall be provided with swing sections or traverse joints or other device which shall absorb the strains or stresses due to the expansion and contraction or vibration of the vertical pipe lines.

- 18-29-308.9  Stacks.

Bases of stacks shall be supported by concrete, brick laid in cement mortar, or metal brackets attached to the building or by other approved methods.

- 18-29-308.10  Parallel water distribution systems.

Piping bundles for manifold systems shall be supported in accordance with Table 18-29-308.5. Support at changes in direction shall be in accordance with the manufacturer's installation instructions. Hot and cold water piping shall not be grouped in the same bundle.

- 18-29-309  Floodproofing.

- 18-29-309.1  General.

Plumbing systems and equipment in structures erected in areas prone to flooding shall be constructed in accordance with the requirements of this section.

- 18-29-309.1.1  Base flood elevation.

The base flood elevation shall be used to define areas prone to flooding and shall be established in accordance with zoning/planning code.

- 18-29-309.2  Deliberately omitted.

- 18-29-310  Washroom and Toilet Room Requirements.

- 18-29-310.1  Ventilation.

Washrooms and toilet rooms shall be ventilated as provided in Chapters 13-172 and 13-176.

- 18-29-310.2  Location of fixtures and piping.

Piping, fixtures or equipment shall not be located in such a manner as to interfere with the normal operation of windows, doors or other means of egress openings.

- 18-29-310.3  Deliberately omitted.

- 18-29-310.4  Water closet compartment.

Each water closet utilized by the public or employees shall occupy a separate compartment with a door and walls or partitions between structures to ensure privacy.

Exception: Water closet compartments shall not be required in a single-occupant toilet room with a lockable door.

- 18-29-311  Toilet Facilities for Workers.

- 18-29-311.1  General; Workmen's temporary closets.

It shall be unlawful for the owner of any building, or any person employing or in charge of any persons, to begin the construction, alteration, or repair of any building, or the construction of any public or private works, without having provided proper and sufficient toilet facilities. Such toilet facilities include water closets, chemical closets, privies, or incinerators of a type to be approved by the Building Department for the use of all employees engaged in the construction, alteration, or repairs of buildings or the construction of any public or private works. There shall be at least one such water closet, chemical closet, privy or incinerator for every 30 employees or fraction thereof. Toilet facilities in multiple story buildings shall be so located that no floor is more than four stories from a story containing toilet facilities. Grade level toilets shall be located not closer than 5 feet from a side lot line.

- 18-29-312  Tests and Inspections.

- 18-29-312.1  Required tests.

Permit holders shall make applicable tests prescribed in Sections 18-29-312.2 through 18-29-312.9 to determine compliance with provisions of this chapter. A permit holder shall give reasonable advance notice to the building commissioner and the commissioner of water management when plumbing work is ready for tests.  The equipment, material, power and labor necessary for the inspection and test shall be furnished by the permit holder and the permit holder shall be responsible for determining that the work will withstand the test pressure prescribed in the following tests.  All plumbing system piping shall be tested with either water, smoke or air.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-312.2  Drainage and vent water test.

The water pressure test for plumbing shall be applied by closing the lower end of the vertical pipes and filling the pipes to the highest opening above the roof with water. The air pressure test for plumbing shall be applied with a force pump and mercury column equal to 10 inches (250 mm) of mercury. The use of spring gauges is prohibited. Special provision shall be made to include all joints and connections to the finished line or face of floors or side walls, so that all vents or revents, including lead work, may be tested with the main stacks. All pipes shall remain uncovered in every part until they have successfully passed the test.

- 18-29-312.3  Deliberately omitted.

- 18-29-312.4  Deliberately omitted.

- 18-29-312.5  Water supply system test.

Upon completion of a section of or the entire water supply system, the system, or portion completed, shall be tested and proved tight under a water pressure not less than the working pressure of the system; or by an air test of not less than 50 psi (344 kpa). The water utilized for tests shall be obtained from a potable source of supply. The required tests shall be performed in accordance with this section and Section 18-29-606.6.

- 18-29-312.6  Gravity sewer test.

Gravity sewer tests shall consist of plugging the end of the building sewer at the last downstream structure before the public main, filling the building sewer with water, testing with not less than a 10 ft (3.05 m) head of water, and maintaining such pressure or level for 15 minutes.

- 18-29-312.7  Forced sewer test.

Forced sewer tests shall consist of plugging the end of the building sewer at the last downstream structure before the public main and applying a pressure of 5 psi (34.5 kPa) greater than the pump rating, and maintaining such pressure for 15 minutes.

- 18-29-312.8  Storm drainage system test.

Storm drain systems within a building shall be tested by water or air in accordance with Section 18-29-312.2.

- 18-29-312.9  Cross connection control device inspections.

The department of water shall inspect backflow prevention assemblies to determine proper installation including testing by a licensed Cross Connection Control Device Inspector. Reduced pressure principle backflow preventer assemblies, double check-valve assemblies, double-detector check-valve assemblies and pressure vacuum breaker assemblies shall be tested at minimum, annually, the results of annual tests shall be reported within 30 days of tests to the department of water. In the event of test failure, immediate notification must be made to the department of water and remedial action taken to prevent the contamination of the potable water supply. The testing procedure shall be performed in accordance with one of the following standards:

ASSE 5010-1013-1, Sections 1 and 2

ASSE 5010-1015-1, Sections 1 and 2

ASSE 5010-1015-2

ASSE 5010-1015-3, Sections 1 and 2

ASSE 5010-1015-4, Sections 1 and 2

ASSE 5010-1020-1, Sections 1 and 2

ASSE 5010-1047-1, Sections 1, 2, 3 and 4

ASSE 5010-1048-1, Sections 1, 2, 3 and 4

ASSE 5010-1048-2

ASSE 5010-1048-3, Sections 1, 2, 3 and 4

ASSE 5010-1048-4, Sections 1, 2, 3 and 4

CSA B64.1.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- Article 4.  Fixtures, Faucets and Fixture Fittings

- 18-29-401  General.

- 18-29-401.1  Scope.

This article shall govern the materials, design and installation of plumbing fixtures, faucets and fixture fittings in accordance with the type of occupancy, and shall provide for the minimum number of fixtures for various occupancies and uses.

- 18-29-401.2  Prohibited fixtures and connections.

Pan, valve, plunger, offset, washout, latrine, frost proof and other water closets having a concealed trap seal or an unventilated space or having walls that are not thoroughly washed at each discharge shall be prohibited. Any water closet that permits siphonage of the contents of the bowl back into the tank shall be prohibited. Trough urinals shall be prohibited. A fixed wooden wash tray or wooden sink shall not be installed or maintained in any building designed or used for human habitation. No metal lined wooden bathtub shall be installed or reconnected.

- 18-29-401.3  Water conservation.

The maximum water flow rates and flush volume for plumbing fixtures and fixture fittings shall comply with Section 18-29-604.4 of this article.

- 18-29-401.4  Separate toilet room.

A room or space containing a urinal, bath or water closet shall be entirely separated from any other room, work space or hall by a solid partition extending from floor to ceiling broken only by the entrance doorway. No window, transom or other opening shall be made from any such room or space into an adjoining room, work space, hallway or compartment of any kind for the purpose of ventilation. Nothing in this section shall preclude the installation of supervised children's toilet areas in day care centers.

- 18-29-402  Fixture Materials.

- 18-29-402.1  Quality of fixtures.

Plumbing fixtures shall be constructed of approved materials, with smooth, impervious surfaces, free from defects and concealed fouling surfaces. Such fixtures shall conform to standards cited in this article. All porcelain enameled surfaces on plumbing fixtures shall be acid resistant.

- 18-29-402.1.1  Used fixtures.

Where used fixtures are to be installed in any new or existing building, such fixtures shall be subject to the inspection and approval of the plumbing inspector. No used plumbing fixture shall be installed in any building unless such fixture is structurally sound and free from cracks or other defects. No sink, toilet, urinal, bathtub, laundry tray, slop sink, or wash bowl which has been used in any building or elsewhere shall be installed in any building, unless such fixture has before installation been thoroughly washed and disinfected in a solution approved by the board of health. The plumbing inspector shall ensure that this provision is strictly enforced and that no used fixture which may cause the spread of infection or disease is installed in any building in this city. No used fixture, even if structurally sound and in sanitary condition, shall be installed in any building in this city, unless such fixture is of the design required by the provisions of this article for a similar new fixture.

- 18-29-402.2  Materials for specialty fixtures.

Materials for specialty fixtures not otherwise covered in this article shall be of stainless steel, soapstone, chemical stoneware or plastic, or shall be lined with lead, copper-base alloy, nickel-copper alloy, corrosion-resistant steel or other material especially suited to the application for which the fixture is intended.

- 18-29-402.3  Sheet copper.

Sheet copper for general applications, shower pans or flashing of fixtures shall conform to ASTM B 152 and shall weigh not less than 12 ounces per square foot (3.7 kg/m2).

- 18-29-402.4  Sheet lead.

Sheet lead for shower pans shall weigh not less than 4 pounds per square foot (19.5 kg/m2) and the sheet lead shall be coated with an asphalt paint or other approved coating.

- 18-29-402.5  Fixture strainer.

Every fixture other than a water closet, pedestal urinal, clinic service sink or hospital fixture and every floor drain, shall be provided with a metallic strainer.

- 18-29-402.6  Fixture overflow.

A new or existing overflow pipe if provided for a fixture, shall be connected on the inlet side of the trap and shall be accessible for cleaning.

- 18-29-403  Minimum Plumbing Facilities.

- 18-29-403.1  Minimum number of fixtures.

Plumbing fixtures shall be provided for each occupancy and use in the minimum number shown in Table 18-29-403.1.  Occupancies and uses not shown in Table 18-29-403.1 shall be considered individually by the building commissioner.  Occupancies and the number of persons (for various occupancies and uses) shall be as determined by Chapter 13-56.

Table 18-29-403.1
Minimum Number of Plumbing Facilities a for New Buildings or Buildings With a Change of Occupancy

For a printer-friendly PDF version of Table 18-29-403.1, please click here.

OCCUPANCY/USE; WATER CLOSETS (Urinals, see Section 419.2); LAVA- TORIES; BATHTUB/ SHOWERS; DRINKING FOUNTAINS (See Section 410.1); OTHERS. Male; Female. A S S E M B L Y; Restaurants and Nightclubs (more than 100); 1 per each 30 to 90; 1 per each 25 up to 100; 1 per 50; –; 1 per 500; 1 service sink. 1 per each 50 above 90; 1 per each 30 above 100. Theaters, halls, museums, coliseums, arenas, etc.; 1 per each 30 up to 60; 1 per each 15 up to 60; –; 1 per 1,000; 1 service sink. 1 per each 70 between 61 and 340; 1 per each 30 between 61 and 340. 1 per each 100 above 340; 1 per each 50 above 340. Churches b; 1 per each 30 up to 90; 1 per each 20 up to 100; –; 1 per 1,000; 1 service sink. 1 per each 50 above 90; 1 per each 25 above 100. Stadiums, etc. (open air); 1 per each 60 up to 240; 1 per each 30 up to 240; 1 per 50; –; 1 per 1,000; 1 service sink. 1 per each 100 between 241 and 1040; 1 per each 50 between 241 and 1040. 1 per each 150 above 1040; 1 per each 75 above 1040. Health Club; 1 per each 30 up to 90; 1 per each 25 up to 100; 1 per 50; 1 per 500; 1 service sink. 1 per each 50 above 90; 1 per each 30 above 100. Business (see Sections 403.2, 403.4 and 403.5); 1 for first 10 2 for 11-25 1 additional for each 25 in excess of 25; 1 per 40; –; 1 per 100; 1 service sink. Educational; –; 1 per 100; 1 service sink. Factory and industrial; (See Section 411); 1 per 400; 1 service sink. High hazard (see Sections 403.2 and 403.4); (See Section 411); 1 per 1,000; 1 service sink. I N S T I T U T I O N A L; Residential care; 1 per 10; 1 per 10; 1 per 8; 1 per 100; 1 service sink. Hospitals, ambulatory nursing home patients c; 1 per room d; 1 per room d; 1 per 15; 1 per 100; 1 service sink per floor. Day nurseries, sanitariums, non-ambulatory nursing home patients, etc. c; 1 per 15; 1 per 15; 1 per 15 e; 1 per 100; 1 service sink. Employees, other than residential care c; 1 per 25; 1 per 35; –; 1 per 100; –. Visitors, other than residential care; 1 per 75; 1 per 100; –; 1 per 500; –. Prisons c; 1 per cell; 1 per cell; 1 per 15; 1 per 100; 1 service sink. Asylums, reformatories, etc. c; 1 per 15; 1 per 15; 1 per 15; 1 per 100; 1 service sink. M E R C A N T I L E; Mercantile – Stores, malls, etc. (see Sections 403.2, 403.4 and 403.5); 1 per each 25 up to 100; 1 per each 15 up to 90; 1 per 40; –; 1 per 1,000; 1 service sink. 1 per each 40 above 100; 1 per each 25 above 90. Mercantile – Restaurants & nightclubs of 100 or less (see Sections 403.2, 403.4 and 403.5); 1 per each 30 to 90; 1 per each 25 up to 100; 1 per 50; –; 1 per 500; 1 service sink. 1 per each 50 above 90; 1 per each 30 above 100. R E S I D E N T I A L; Hotels, motels; 1 per guestroom; 1 per guest- room; 1 per guestroom; –; 1 service sink. Lodges; 1 per 10; 1 per 10; 1 per 8; 1 per 100; 1 service sink. Multiple family; 1 per dwelling unit; 1 per dwelling unit; 1 per dwelling unit; –; 1 kitchen sink per dw. unit., 1 auto. clothes washer connect per 20 dw. units. Dormitories; 1 per 10; 1 per 10; 1 per 8; 1 per 100; 1 service sink. One- and two-family dwellings; 1 per dwelling unit; 1 per dwelling unit; 1 per dwelling unit; –; 1 kitchen sink per dw. unit.; 1 auto. clothes washer connection per dwelling unit f. Storage (see Sections 403.2 and 403.4); 1 per 100; 1 per 100; (see Section 411); 1 per 1,000; 1 service sink.

a The fixtures shown are based on one fixture being the minimum required for the number of persons indicated or any fraction of the number of persons indicated. The number of occupants shall be determined by the building code.

b Fixtures located in adjacent buildings under the ownership or control of the church shall be made available during periods the church is occupied.

c Toilet facilities for employees shall be separate from facilities for inmates or patients.

d A single-occupant toilet room with one water closet and one lavatory serving not more than two adjacent patient rooms shall be permitted where such room is provided with direct access from each patient room and with provisions for privacy.

e For day nurseries, a maximum of one bathtub shall be required.

f For attached one- and two-family dwellings, one automatic clothes washer connection shall be required per 20 dwelling units.

(Amend Coun. J. 3-27-02, p. 82090, § 3; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-403.2  Separate facilities.

Where plumbing fixtures are required, separate facilities shall be provided for both genders.

Exceptions:

1.     Separate facilities shall not be required in residential occupancies.

2.     Separate employee facilities shall not be required in occupancies in which five or less people are employed.

3.     Separate facilities shall not be required in structures or tenant spaces in which food or beverage is served for consumption within the structure or tenant space when the total occupant load is five or less, including both employees and customers.

- 18-29-403.3  Number of occupants for both genders.

The required water closets, lavatories, and showers or bathtubs shall be distributed equally between genders based on the percentage of both genders anticipated in the occupant load.  The occupant load shall be composed of 50 percent for both genders, unless statistical data approved by the building commissioner indicate a different distribution of both genders.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-403.4  Location of employee toilet facilities in occupancies other than assembly or mercantile.

Access to toilet facilities in occupancies other than mercantile and assembly occupancies shall be located within the employees' regular working area. The required toilet facilities shall be located not more than one story above or below the employees' regular working area and the path of travel to such facilities shall not exceed a distance of 200 feet (61 m). Employee facilities shall be either separate facilities or public customer facilities.

Exception: Facilities that are required for employees in storage structures or kiosks, situated in adjacent structures under the same ownership, lease or control, shall be located at a maximum travel distance of 500 feet (152 m) from the employees' regular working area.

- 18-29-403.5  Toilet facilities in mercantile and assembly occupancies.

Employees shall be provided with toilet facilities in buildings and tenant spaces utilized as restaurants, nightclubs, places of public assembly and mercantile occupancies. The employee facilities shall be either separate facilities or public customer facilities.

Exception: Employee toilet facilities shall not be required in tenant spaces of 900 square feet (84 m2) or less where the travel distance from the main entrance of the tenant space to a central toilet area does not exceed 200 feet (61 m) and such central toilet facilities are located not more than one story above or below the tenant space.

- 18-29-403.6  Customer facilities.

Customers, patrons and visitors shall be provided with public toilet facilities in structures and tenant spaces intended for public use and utilized as restaurants, nightclubs, places of assembly, business and mercantile occupancies. Customer toilet facilities shall be located not more than one story above or below the space required to be provided with customer toilet facilities and the path of travel to such facilities shall not exceed a distance of 200 feet (61 m). In covered mall buildings, required facilities shall be based on total square footage, and facilities shall be installed in each individual store or in a central toilet area located in accordance with this section. The maximum travel distance to the central toilet facilities in covered mall buildings shall be measured from the main entrance of any store or tenant space.

Exception: Toilet facilities for the public shall not be required in mercantile units of less than seven thousand five hundred (7500) square feet in gross area. In mercantile units of seven thousand five hundred (7500) square feet or more in gross area the occupancy content shall be determined by dividing the net floor area used by the public, as shown in an actual floor plan layout, by one hundred (100), or a minimum of twenty- five percent (25%) of the gross area whichever is smaller.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-403.6.1  Pay facilities.

Required facilities shall be free of charge and designated by legible signs for both genders. It is prohibited to charge any sum of money for the use of any toilet facility in any municipally owned building or any building that is open to accommodate or serve the public.

- 18-29-403.6.1.1  Included buildings.

As used herein, “building that is open to accommodate or serve the public” shall include the following: hotel, motel, inn, department store, restaurant, cafeteria, lunchroom, lunch counter, soda fountain, tavern, motion picture house, theater, concert hall, sports arena, stadium or other place of exhibition or entertainment, airport, railroad station or terminal, bus station or terminal, clothing store, food store, gas station, garage, bank or office building.

- 18-29-403.7  Drinking fountains.

Drinking fountains shall be of an approved type and shall be located on the same floor or one floor above or below and within 200 feet (61 m) of all locations at which workers are regularly employed. No bubbler shall be installed on or above any plumbing fixture other than a drinking fountain. No drinking fountain or bubbler shall be installed in any toilet room, except in penal institutions.

- 18-29-403.8  Multiple dwellings.

In multiple dwellings and institutional units, toilet rooms shall be provided on every floor having sleeping accommodations.

- 18-29-403.9  Kitchens.

Except in family units, no bathroom or toilet room shall open directly into a room where food is prepared, stored or served without an intervening vestibule.

- 18-29-404  Accessible Plumbing Facilities.

- 18-29-404.1  Where required.

Accessible plumbing facilities and fixtures shall be in compliance with the Illinois Accessibility Code.

- 18-29-405  Installation of Fixtures.

- 18-29-405.1  Water supply protection.

The supply lines and fittings for every plumbing fixture shall be installed so as to prevent backflow.

- 18-29-405.2  Access for cleaning.

Plumbing fixtures shall be installed so as to afford easy access for cleaning both the fixture and the area around the fixture. All traps not integral with the fixtures shall be accessible for cleaning. When a “P” trap is used on a bath waste it shall be directly below the tub overflow. The overflow shall be fastened to the tub by means other than the face plate. Face plates shall be clearly marked “clean out.”

- 18-29-405.2.1  Toilet room construction.

Rooms or spaces containing water closets, urinals, bathtubs, or showers shall have floors of nonabsorbent materials and shall be entirely separated from other rooms by solid partitions extending from floor to ceiling without openings, except as required for access or mechanical ventilation.

- 18-29-405.2.2  Day care centers.

The requirement for floor-to-ceiling partitions shall not apply to day care centers where supervised boys' and girls' toilets are provided exclusively for children under six years of age. Such supervised children's toilet areas adjacent to and serving one or more classrooms shall be grouped into boys toilets and girls' toilets. Boys' and girls' toilets shall be separated from the other and from the classrooms by modesty panels at least 4 feet (1220 mm) high and shall utilize special children's water closets. Lavatories shall be located in a common vestibule serving separate boys' and girls' toilets.

- 18-29-405.3  Setting.

Fixtures shall be set level and in proper alignment with reference to adjacent walls.

- 18-29-405.3.1  Water closets, lavatories and bidets.

A water closet, lavatory or bidet shall not be set closer than 15 inches (380 mm) from its center to any side wall, partition, vanity or other obstruction, or closer than 30 inches (760 mm) center-to-center between toilets or adjacent fixtures. There shall be at least 18 inches (457 mm) clearance in front of the water closet or bidet to any wall, fixture or door. Water closet compartments shall not be less than 30 inches (760 mm) wide and 60 inches (1525 mm) deep. There shall be at least 8 inches (457 mm) clearance in front of a lavatory to any wall, fixture or door (see Figure 18-29-405.3.1).

- 18-29-405.3.2  Urinals.

A urinal shall not be set closer than 15 inches (381 mm) from the center of the urinal to any side wall, partition, vanity or other obstruction, or closer than 30 inches (760 mm) center-to-center between urinals (see Figure 18-29-405.3.1).

Figure 18-29-405.3.1
Fixture Clearances

For SI: 1 inch = 25.4 mm

- 18-29-405.4  Floor and wall drainage connections.

Connections between the drain and floor outlet plumbing fixtures shall be made with a floor flange. The flange shall be attached to the drain and anchored to the structure. Connections between the drain and wall-hung water closets shall be made with an approved extension nipple or horn adapter. The water closet shall be bolted to the hanger with corrosion-resistant bolts or screws. Joints shall be sealed with an approved elastomeric gasket or setting compound conforming to FS TT- P-1536a.

- 18-29-405.4.1  Floor flanges.

Floor flanges for water closets or similar fixtures shall be not less than 1/8 inch (3 mm) thick for brass, 1/4 inch (6 mm) thick for plastic, and 1/4 inch (6 mm) thick and not less than a 2-inch (50 mm) caulking depth for cast-iron or galvanized malleable iron.

- 18-29-405.4.1.1  Hard lead floor flanges.

Floor flanges of hard lead shall weigh not less than 1 pound 9 ounces (0.7 kg) and shall be composed of lead alloy with not less than 7.75 percent antimony by weight. Closet screws and bolts shall be of brass. Flanges shall be secured to the building structure with corrosion-resistant screws or bolts.

- 18-29-405.4.2  Securing floor outlet fixtures.

Floor outlet fixtures shall be secured to the floor or floor flanges by screws or bolts of corrosion-resistant material.

- 18-29-405.4.3  Securing wall-hung water closet bowls.

Wall-hung water closet bowls shall be supported by a concealed metal carrier that is attached to the building structural members so that strain is not transmitted to the closet connector or any other part of the plumbing system. The carrier shall conform to ASME A112.6.1.

- 18-29-405.5  Water-tight joints.

Joints formed where fixtures come in contact with walls or floors shall be sealed with permanent caulk or other approved material.

- 18-29-405.6  Plumbing in mental health centers.

In mental health centers, pipes or traps shall not be exposed, and fixtures shall be bolted through walls.

- 18-29-405.7  Design of overflows.

Where any fixture is provided with an overflow, the waste shall be designed and installed so that standing water in the fixture will not rise in the overflow when the stopper is closed, and no water will remain in the overflow when the fixture is empty.

- 18-29-405.7.1  Connection of overflows.

The overflow from any fixture shall discharge into the drainage system on the inlet or fixture side of the trap.

Exception: The overflow from a flush tank serving a water closet or urinal shall discharge into the fixture served.

- 18-29-405.8  Access to concealed connections.

Fixtures with concealed slip joint connections shall be provided with an access panel or utility space at least 12 inches (300 mm) in its smallest dimension or other approved arrangement so as to provide access to the slip connections for inspection and repair. Where such access cannot be provided, access doors shall not be required provided that all joints are soldered, solvent cemented or screwed so as to form a solid connection.

- 18-29-406  Automatic Clothes Washers.

- 18-29-406.1  Approval.

Domestic automatic clothes washers shall conform to ASSE 1007.

- 18-29-406.2  Water connection.

The water supply to an automatic clothes washer shall be protected against backflow by an air gap installed integrally within the machine conforming to ASSE 1007 or with the installation of a backflow preventer in accordance with Article 18-296.

- 18-29-406.3  Waste connection.

The discharge from an automatic clothes washer shall be through an air break and connected to a standpipe in accordance with Article 8.

- 18-29-407  Bathtubs.

- 18-29-407.1  Approval.

Bathtubs shall conform to ANSI Z124.1, ASME A112.19.1, ASME A112.19.4, ASME A112.19.9, CSA B45.2, CSA B45.3 or CSA B45.5.

- 18-29-407.2  Bathtub waste outlets.

Bathtubs shall have waste outlets a minimum of 1 1/2 inches (40 mm) in diameter. The waste outlet shall be equipped with an approved stopper.

- 18-29-407.3  Glazing.

Windows and doors within a bathtub enclosure shall conform to the safety glazing requirements of Section 13-124-350.

- 18-29-408  Bidets.

- 18-29-408.1  Approval.

Bidets shall conform to ASME A112.19.2, ASME A112.19.9 or CSA B45.1.

- 18-29-408.2  Water connection.

The water supply to a bidet shall be protected against backflow by an air gap or backflow preventer in accordance with Article 18-29-6.

- 18-29-409  Dishwashing Machines.

- 18-29-409.1  Approval.

Domestic dishwashing machines shall conform to ASSE 1006. Commercial dishwashing machines shall conform to ASSE 1004.

- 18-29-409.2  Water connection.

The water supply to a dishwashing machine shall be protected against backflow by an air gap or backflow preventer in accordance with Article 18-29-6.

- 18-29-409.2.1  Water supply connection.

The water supply to commercial dishwashing machines shall be connected through an air gap or by means of proper backflow protection, e.g., a nonpressure type (atmospheric) vacuum breaker or a dual check valve backflow preventer assembly (DuC), depending upon the circumstances.

- 18-29-409.2.2  Hot water.

A commercial dishwashing machine or similar dishwashing equipment that relies upon hot water for sanitizing dishes and utensils, rather than chemicals for sanitizing, shall provide rinse water at 180°F (82.2°C).

Exception: A single-tank, stationary-rack, single temperature dishwashing machine shall provide a rinse water temperature of 165°F (73.8°C).

- 18-29-409.3  Waste connection.

When a domestic (private residence) dishwashing machine drain line is connected to the house side of a trap from a sink, the drain from the dishwasher shall be carried up to the underside of the spill rim of the sink. Dishwashing machines shall discharge separately into a trap or tail piece of the kitchen sink and shall not connect to the food waste disposal unit.

- 18-29-409.3.1  Commercial dishwashers.

Commercial dishwashing machines shall indirectly discharge to a proper receptor connected to the drainage system, or may be hard connected provided the dishwashing machine is on a separate branch and an in- line floor drain is installed immediately downstream of the dishwasher connection.

- 18-29-410  Drinking Fountains.

- 18-29-410.1  Approval.

Drinking fountains shall conform to ASME A112.19.1, A112.19.2 or A112.19.9, and water coolers shall conform to ARI 1010. Where water is served in restaurants drinking fountains shall not be required.

- 18-29-410.2  Prohibited location.

Drinking fountains shall not be installed in public restrooms.

- 18-29-411  Emergency Showers and Eyewash Stations.

- 18-29-411.1  Water connection.

Emergency eyewash stations shall be provided with a supply of cold water as required by the manufacturer. Emergency showers shall be provided with a supply of tempered water in accordance with ANSI Z358.1.

- 18-29-411.2  Waste connection.

Emergency showers and eye wash stations within a building shall be provided with a trapped and vented receptor.

- 18-29-412  Floor Drains.

- 18-29-412.1  Approval.

Floor drains shall conform to ASME A112.21.1 or CSA B79.

- 18-29-412.2  Floor drain trap and strainer.

Floor drain traps shall have removable strainers. The strainer shall have a waterway area of not less than the area of the tailpiece. The floor drain shall be constructed so that the drain is capable of being cleaned. Access shall be provided to the drain inlet.

- 18-29-412.3  Size of floor drains.

Floor drains shall have a minimum 2-inch diameter (50 mm) drain outlet.

- 18-29-412.4  Required location and construction.

Any building or structure in which plumbing is installed under a concrete floor or concrete over a crawl space shall have at least one trapped floor drain. Additional floor drains shall be required if the installation of fixtures and appurtenances requires the use of floor drains. In a multifamily dwelling, each unit shall have a floor drain if fixtures and appurtenances installed therein require the use of a floor drain.

- 18-29-412.4.1  Underground floor drains.

Underground floor drains connected to a building drain or a building sub-drain within 4 feet (1220 mm) of a stack shall be individually vented. All other floor drains shall be vented as required by Article 18-29-9.

- 18-29-412.4.2  Sanitary waste drain.

Each floor drain shall be connected to a sanitary waste drain. Area drains should not connect to any subsoil drainage system, but may be connected to the storm drainage system where they receive storm drainage exclusively.

- 18-29-412.4.3  Masonry or concrete floor.

At least one floor drain shall be located in every restroom having a masonry or concrete floor except those for private use.

- 18-29-412.4.4  Hospitals and nursing homes.

In hospitals and nursing homes, floor drains will not be required in toilet/bath facilities serving four or fewer individual residents where access to the facilities is direct from no more than two resident rooms. Toilet/bath facilities in hospitals and nursing homes serving rooms with greater than four residents or consisting of multiple toilets, lavatories. etc., are required to have floor drains.

- 18-29-412.4.5  Public laundries and multiple-family dwellings.

In public coin-operated laundries and in the central washing facilities of multifamily dwellings, rooms containing the automatic clothes washers shall be provided with floor drains located to readily drain the entire floor area. Such drains shall have a minimum outlet cross section of not less than 3 inches (76 mm) in diameter.

- 18-29-412.4.6  Size.

Each floor drain shall be sized for its intended use and the surface area that it drains. Any floor drain or drain trap installed below a basement floor or underground shall be no less than 3 inches (76 mm) in diameter.

- 18-29-412.4.7  Accessibility.

Floor drains shall connect into traps, shall be accessible and readily cleaned, and shall be located so that they are easily visible.

- 18-29-412.4.8  Provision for evaporation.

Floor drain seals subject to evaporation shall be of the deep seal type, shall be fed by means of a priming device designed for that purpose, or shall be filled with vegetable oil.

- 18-29-412.4.9  Floor drains in food establishments.

If floor drains are installed in coolers, freezers, refrigerated holding areas, dressing rooms or processing rooms in any food (meat, milk, vegetable, fruit) establishment, they shall meet the following requirements:

1.     Floor drains shall have a minimum inside diameter of 4 inches (102 mm) and be of metallic construction.

2.     Drainage lines from water closets and urinals shall not be connected with any other sanitary drainage lines having floor drains located in the above places within the building.

3.     Floor drains must be indirectly discharged to the drainage system, or a backwater valve that conforms with the requirements of Article 18-29-8.

- 18-29-413  Food Waste Grinder Units.

- 18-29-413.1  Approval.

Domestic food waste grinders shall conform to ASSE 1008. Commercial food waste grinders shall conform to ASSE 1009. Food waste grinders shall not increase the drainage fixture unit load on the sanitary drainage system.

- 18-29-413.2  Domestic food waste grinder waste outlets.

Domestic food waste grinders shall be connected to a drain of not less than 1 1/2 inches (40 mm) in diameter.

- 18-29-413.3  Commercial food waste grinder waste outlets.

Commercial food waste grinders shall be connected to a drain a minimum of 2 inches (50 mm) in diameter. Commercial food waste grinders shall be connected and trapped separately from any other fixtures or sink compartments.

- 18-29-413.4  Water supply required.

All food waste grinders shall be provided with a supply of cold water.

- 18-29-414  Garbage Can Washers.

- 18-29-414.1  Water connection.

The water supply to a garbage can washer shall be protected against backflow by an air gap or a backflow preventer in accordance with Section 18-29-608.13.1, Section 18-29-608.13.2, Section 18-29-608.13.3, Section 18-29-608.13.5, Section 18-29-608.14 or Section 18-29-608.15.

- 18-29-414.2  Waste connection.

Garbage can washers shall be trapped separately. The receptacle receiving the waste from the washer shall have a removable basket or strainer to prevent the discharge of large particles into the drainage system.

- 18-29-415  Laundry Trays.

- 18-29-415.1  Approval.

Laundry trays shall conform to ANSI Z124.6, ASME A112.19.1, ASME A112.19.3, ASME A112.19.9, CSA B45.2 or CSA B45.4.

- 18-29-415.2  Waste outlet.

Each compartment of a laundry tray shall be provided with a waste outlet a minimum of 1 1/2 inches (38 mm) in diameter and a strainer or crossbar to restrict the clear opening of the waste outlet.

- 18-29-416  Lavatories.

- 18-29-416.1  Approval.

Lavatories shall conform to ANSI Z124.3, ASME A112.19.1, ASME A112.19.2, ASME A112.19.3, ASME A112.19.4, ASME A112.19.9, CSA B45.1, CSA B45.2, CSA B45.3 or CSA B45.4. Group wash-up equipment shall conform to the requirements of Section 18-29-402. Every 20 inches (500 mm) of rim space shall be considered as one lavatory.

- 18-29-416.2  Cultured marble lavatories.

Cultured marble vanity tops with an integral lavatory shall conform to ANSI Z124.3 or CSA B45.5.

- 18-29-416.3  Lavatory waste outlets.

Lavatories shall have waste outlets not less than 1 1/4 inches (32 mm) in diameter. A strainer, pop-up stopper, crossbar or other device shall be provided to restrict the clear opening of the waste outlet.

- 18-29-417  Showers.

- 18-29-417.1  Approval.

Prefabricated showers and shower compartments shall conform to ANSI Z124.2, ASME A112.19.9 or CSA B45.5. Shower valves for individual showers shall conform to the requirements of Section 18-29-424.4.

- 18-29-417.2  Water supply riser.

Every water supply riser from the shower valve to the shower head outlet, whether exposed or not, shall be attached to the structure in an approved manner.

- 18-29-417.3  Shower waste outlet.

Waste outlets serving showers shall be at least 2 inches (50 mm) in diameter and, for other than waste outlets in bathtubs, shall have removable strainers not less than 3 inches (75 mm) in diameter with strainer openings not less than 1/4 inch (6 mm) in minimum dimension. Where each shower space is not provided with an individual waste outlet, the waste outlet shall be located and the floor pitched so that waste from one shower does not flow over the floor area serving another shower. Waste outlets shall be fastened to the waste pipe in an approved manner.

- 18-29-417.4  Shower compartments.

Shower installation, water temperature, dimensions, materials, public or institutional showers, and wall areas shall comply with Sections 18-29-417.4.1 through 18-29-417.4.7.

- 18-29-417.4.1  Deliberately omitted.

- 18-29-417.4.2  Wall area.

The wall area above built-in tubs with installed shower heads and in shower compartments shall be constructed of smooth, noncorrosive and nonabsorbent waterproof materials to a height not less than 72 inches (1829 mm) above the room floor level, and not less than 70 inches (1778 mm) where measured from the compartment floor at the drain. Such walls shall form a water-tight joint with each other and with either the tub, receptor or shower floor.

- 18-29-417.4.3  Shower installation.

Traps shall be constructed so that the pan is fastened to the trap at the seepage entrance, making a water-tight joint between the pan and the trap. Shower receptacle waste outlets shall be at least 2 inches (50mm) in diameter and have a removable strainer.

- 18-29-417.4.4  Water temperature safety.

All shower compartments and shower-bath combinations shall be provided with an automatic safety water mixing device to prevent sudden unanticipated changes in water temperature or excessive water temperatures. The automatic safety water mixing device shall be either thermostatic, pressure balance, or combination controlled, in accordance with ANSI/ASSE 1016-1990, and designed with a maximum handle rotation limit/stop, adjusted to a maximum setting of 115°F (46.1°C) at the time of installation. The temperature of mixed water provided to multi-shower units or gang showers shall be controlled by a master automatic safety water mixing device or the mixed water temperature for such showers shall be individually regulated by automatic safety mixing valves for each shower unit. A hot water heater thermostat shall not be an acceptable alternative water temperature control device.

- 18-29-417.4.5  Dimensions.

Single-family shower compartments or stalls shall have at least 1,024 square inches (6606 cm2) outside dimension (O.D.) floor area and shall be at least 32 inches (813 mm) in shortest outside dimension. All other shower compartments or stalls shall have no less than 1,296 square inches (3292 cm2) outside dimension floor area and shall be at least 32 inches (813 mm) in shortest outside dimension.

- 18-29-417.4.6  Materials.

Shower walls shall be constructed of durable, smooth, nonabsorbent, noncorrosive, and waterproof materials, such as fiberglass, enameled metal, or plastic sheeting. All shower compartments or stalls shall have a slip resistant floor (bottom) surface.

- 18-29-417.4.7  Public or institution showers.

Floors of public shower rooms shall be drained so that no waste water from any bather will pass over areas occupied by other bathers. This shall not prohibit the use of column showers.

- 18-29-417.5  Shower floor or receptors.

Floor surfaces or receptors shall comply with the following requirements:

- 18-29-417.5.1  Support.

Floors or receptors under shower compartments shall be laid on, and supported by, a smooth and structurally sound base. Support for shower compartments shall comply with the following requirements:

1.     Plasticized polyvinyl chloride (PVC) sheet shall be a minimum of 0.040 inch (1 mm) thick, and shall meet the requirements of ASTM D 4551. Sheets shall be joined by solvent welding in accordance with the manufacturer's instructions.

2.     Non-plasticized chlorinated polyethylene (PE) sheet shall be a minimum 0.040 inch (1.02 mm) thick.

3.     Other materials of similar durability and water resistance may be used provided they are approved by the buildings commissioner.

- 18-29-417.5.2  Deliberately omitted.

- 18-29-417.6  Glazing.

Windows and doors within a shower enclosure shall conform to the safety glazing requirements of the building code.

- 18-29-418  Sinks.

- 18-29-418.1  Approval.

Sinks shall conform to ANSI Z124.6, ASME A112.19.1, ASME A112.19.2, ASME A112.19.3, ASME A112.19.4, ASME A112.19.9, CSA B45.1, CSA B45.2, CSA B45.3 or CSA B45.4.

- 18-29-418.2  Sink waste outlets.

Sinks shall be provided with waste outlets a minimum of 1 1/2 inches (38 mm) in diameter. A strainer or crossbar shall be provided to restrict the clear opening of the waste outlet. Sinks on which a food waste grinder is installed shall have a waste opening a minimum of 3 1/2 inches (89 mm) in diameter.

- 18-29-418.2.1  Facilities with no range oven.

Sinks installed in lunchrooms, pantries, break rooms and other similar facilities where no range or oven is installed shall not be required to have a grease interceptor. Installation of a microwave oven in such facilities shall require the installation of a grease interceptor.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-419  Urinals.

- 18-29-419.1  Approval.

Urinals shall conform to ASME A112.19.2, CSA B45.1 or CSA B45.5. Urinals shall conform to the water consumption requirements of Section 18-29-604.4. Urinals shall conform to the hydraulic performance requirements of ASME A 112.19.6, CSA B45.1 or CSA B45.5.

- 18-29-419.2  Substitution for water closets.

In each bathroom or toilet room, urinals shall not be substituted for more than 50 percent of the required water closets.

- 18-29-419.3  Urinals for public or employee toilet facilities.

Urinals for public or employee toilet facilities shall have a visible trap seal.

- 18-29-419.4  Surrounding material.

Wall and floor space to a point 2 feet (610 mm) in front of a urinal lip and 4 feet (1219 mm) above the floor and at least 2 feet (610 mm) to each side of the urinal shall be waterproofed with a smooth, readily cleanable, nonabsorbent material.

- 18-29-420  Water Closets.

- 18-29-420.1  Approval.

Water closets shall conform to the water consumption requirements of Section 18-29-604.4 and shall conform to ANSI Z124.4, ASME A112.19.2, CSA B45.1, CSA B45.4 or CSA B45.5. Water closets shall conform to the hydraulic performance requirements of ASME A112.19.6. Water closet tanks shall conform to ANSI Z124.4, ASME A112.19.2, ASME A112.19.9, CSA B45.1, CSA B45.4 or CSA B45.5.

- 18-29-420.2  Water closets for public or employee toilet facilities.

Water closet bowls for public or employee toilet facilities shall be of the elongated type.

- 18-29-420.3  Water closet seats.

Water closets shall be equipped with seats of smooth non-absorbent material. All seats of water closets provided for public use shall be an antimicrobial plastic material and an open-front style, except closed- front seats may be provided if the seat is encased with a continuous plastic sleeve ensuring a clean surface for every user. No water closet seat shall be more than 1 1/2 (40 mm) inches thick.

Exception: Facilities for the physically disabled shall comply with the Illinois Accessibility Code.

- 18-29-420.4  Water closet connections.

A 4-inch by 3-inch (100 mm by 75 mm) closet bend shall be acceptable. Where a 3-inch (75 mm) bend is utilized on water closets, a 4-inch by 3-inch (100 mm by 75 mm) flange shall be installed to receive the fixture horn.

- 18-29-420.5  Deliberately omitted.

- 18-29-420.6  Chemical closets.

No chemical closet or toilet shall be installed within any building for human habitation, nor on any premises abutting upon a public way or thoroughfare in which a public sewer is available.

- 18-29-420.7  Temporary toilet facilities.

Every tent or structure provided for the temporary accommodations of the public, shall be provided, if access can be made to sewer and water, with not less than one water closet for males, and one water closet for females for each 300 persons or fraction thereof of the total capacity of the tent or structure. If access cannot be had to sewer and water, chemical toilets and incinerators shall be provided in the ratio above required.

- 18-29-421  Whirlpool Bathtubs.

- 18-29-421.1  Approval.

Whirlpool bathtubs shall comply with ASME A112.19.7 or with CSA B45.5 and CSA CAN/CSA-B45 (Supplement 1).

- 18-29-421.2  Installation.

Whirlpool bathtubs shall be installed and tested in accordance with the manufacturer's installation instructions. The pump shall be located above the wire of the fixture trap. Access shall be provided to the pump.

- 18-29-421.3  Drain.

The pump drain and circulation piping shall be sloped to drain the water in the volute and the circulation piping when the whirlpool bathtub is empty.

- 18-29-421.4  Suction fittings.

Suction fittings for whirlpool bathtubs shall comply with ASME A112.19.8.

- 18-29-422  Health Care Fixtures and Equipment.

- 18-29-422.1  Scope.

Sections 18-29-422.9 and 18-29-422.10 shall govern those aspects of health care plumbing systems that differ from plumbing systems in other structures. Health care plumbing systems shall conform to the requirements of this section in addition to the other requirements of this article. The provisions of this section shall apply to the special devices and equipment installed and maintained in the following occupancies: nursing homes, homes for the aged, orphanages, infirmaries, first aid stations, psychiatric facilities, clinics, professional offices of dentists and doctors, mortuaries, educational facilities, surgery, dentistry, research and testing laboratories, establishments manufacturing pharmaceutical drugs and medicines, and other structures with similar apparatus. Refer to the Illinois Department of Public Health requirements for licensing of facilities.

- 18-29-422.2  Deliberately omitted.

- 18-29-422.3  Deliberately omitted.

- 18-29-422.4  Deliberately omitted.

- 18-29-422.5  Deliberately omitted.

- 18-29-422.6  Deliberately omitted.

- 18-29-422.7  Deliberately omitted.

- 18-29-422.8  Deliberately omitted.

- 18-29-422.9  Sterilizer equipment requirements.

All sterilizers shall conform to the requirements of the mechanical article.

- 18-29-422.9.1  Sterilizer piping.

Access for the purposes of inspection and maintenance shall be provided to all sterilizer piping and devices necessary for the operation of sterilizers.

- 18-29-422.9.2  Steam supply.

Steam supplies to sterilizers, including those connected by pipes from overhead mains or branches, shall be drained to prevent any moisture from reaching the sterilizer. The condensate drainage from the steam supply shall be discharged by gravity.

- 18-29-422.9.3  Steam condensate return.

Steam condensate returns from sterilizers shall be a gravity return system.

- 18-29-422.9.4  Condensers.

Pressure sterilizers shall be equipped with a means of condensing and cooling the exhaust steam vapors. Nonpressure sterilizers shall be equipped with a device that will automatically control the vapor, confining the vapors within the vessel.

- 18-29-422.10  Special elevations.

Control valves, vacuum outlets and devices protruding from a wall of an operating, emergency, recovery, examining or delivery room, or in a corridor or other location where patients are transported on a wheeled stretcher, shall be located at an elevation that prevents bumping the patient or stretcher against the device.

- 18-29-423  Specialty Plumbing Fixtures.

- 18-29-423.1  Water connections.

Baptisteries, ornamental and lily pools, aquariums, ornamental fountain basins, swimming pools, and similar constructions, where provided with water supplies, shall be protected against backflow in accordance with Section 18-29-608.

- 18-29-423.2  Approval.

Specialties requiring water and waste connections shall be submitted for approval.

- 18-29-424  Faucets and Other Fixture Fittings.

- 18-29-424.1  Approval.

Faucets and fixture fittings shall conform to ASME A112.18.1 or CSA CAN/CSA-B125 and shall conform to the water consumption requirements of Section 18-29-604.4. Faucets and fixture fittings that supply drinking water for human ingestion shall conform to the requirements of ANSI/NSF 61, Article 18-29-9.

- 18-29-424.2  Hose spray.

Sink faucets with a flexible hose and spray assembly shall conform to ASSE 1025 or CSA CAN/CSA-B 125.

- 18-29-424.3  Hand showers.

Hand-held showers shall conform to ASSE 1014 or CSA CAN/CSA-B125.

- 18-29-424.4  Shower valves.

Shower and tub-shower combination valves shall be either balanced pressure, thermostatic or combination mixing valves that conform to the requirements of ASSE 1017 or CSA CAN/CSA-B 125. Such valves shall be equipped with handle position stops that are field adjusted in accordance with the manufacturer's instructions to a maximum hot water setting of 120°F (495°C).

Exception: Balanced pressure, thermostatic or combination mixing valves shall not be required for showers and tub-shower combinations in multiple showers supplied with a single tempered water supply, provided the hot water supply for such showers is controlled by an approved master thermostatic mixing valve adjusted in accordance with the manufacturer's instructions to a maximum hot water setting of 120°F (495°C). Such master thermostatic mixing valves shall be sized according to the peak demand of fixtures located downstream of the valve and shall comply with ASSE 1017. The water heater thermostat shall not be used as the temperature-control device for compliance with this section.

- 18-29-425  Flushing Devices for Water Closets and Urinals.

- 18-29-425.1  Flushing devices required.

Each water closet, urinal, clinical sink and any, plumbing fixture that depends on trap siphonage to discharge the fixture contents to the drainage system shall be provided with a flushometer valve, flushometer tank or a flush tank designed and installed to supply water in quantity and rate of flow to flush the contents of the fixture, cleanse the fixture and refill the fixture trap.

- 18-29-425.1.1  Separate for each fixture.

A flushing device shall not serve more than one fixture.

- 18-29-425.2  Flushometer valves and tanks.

Flushometer valves and tanks shall comply with ASSE 1037. Vacuum breakers on flushometer valves shall conform to the performance requirements of ASSE 1001 or CSA CAN/CSA-B64.1.1. Access shall be provided to vacuum breakers. Flushometer valves shall be of the water-conservation type and shall not be utilized where the water pressure is lower than the minimum required for normal operation. When operated, the valve shall automatically complete the cycle of operation, opening fully and closing positively under the water supply pressure. Each flushometer valve shall be provided with a means for regulating the flow through the valve. The trap seal to the fixture shall be automatically refilled after each valve flushing cycle.

- 18-29-425.3  Flush tanks.

Flush tanks equipped for manual flushing shall be controlled by a device designed to refill the tank after each discharge and to shut off completely the water flow to the tank when the tank is filled to operational capacity. The trap seal to the fixture shall be automatically refilled after each flushing. The water supply to flush tanks equipped for automatic flushing shall be controlled with a timing device or sensor control devices.

- 18-29-425.3.1  Ball cocks.

All flush tanks shall be equipped with an antisiphon ball cock conforming to ASSE 1002 or CSA CAN/CSA- B125. The ball cock backflow preventer shall be located at least 1 inch (25 mm) above the full opening of the overflow pipe. A sheathed ball cock shall be installed in all gravity flush tanks in which the flush valve seat is located less than 1 inch (25 mm) above the flood level rim of the bowl.

- 18-29-425.3.2  Overflows in flush tanks.

Flush tanks shall be provided with overflows discharging to the water closet or urinal connected thereto and shall be sized to prevent flooding the tank at the maximum rate at which the tanks are supplied with water. The opening of the overflow pipe shall be located above the flood level rim of the water closet or urinal or above a secondary overflow in the flush tank.

- 18-29-425.3.3  Sheet copper.

Sheet copper utilized for flush tank linings shall conform to ASTM B152 and shall not weigh less than 10 ounces per square foot (0.03 kg/m2).

- 18-29-425.3.4  Access required.

All parts in a flush tank shall be accessible for repair and replacement.

- 18-29-425.4  Flush pipes and fittings.

Flush pipes and fittings shall be of nonferrous material and shall conform to ASME A112.19.5 or CSA CAN/CSA-B125.

- Article 5.  Water Heaters

- 18-29-501  General.

- 18-29-501.1  Scope.

The provisions of this article shall govern the materials, design and installation of water heaters and the related safety devices and appurtenances.

- 18-29-501.2  Deliberately omitted.

- 18-29-501.3  Drain valves.

Each heated water storage tank shall be provided with a sludge drain pipe which shall be connected at the lowest level of the bottom section of the tank. This drain shall be provided with a control valve with a clear waterway equal to the area of the sludge drain pipe, and shall discharge through an indirect connection into the drainage system of the building. Drain valves shall conform to ASSE 1005.

- 18-29-501.4  Location for access.

Water heaters and storage tanks shall be located and connected so as to provide access for observation, maintenance, servicing and replacement.

- 18-29-501.5  Water heater labeling.

All water heaters shall bear the label of an approved agency. Listing by Underwriters Laboratories, American Gas Association (AGA), National Board of Boiler and Pressure Vessel Inspectors, or the ASME Standard to which it was constructed, shall constitute evidence of conformance with these standards.

- 18-29-501.6  Tankless water heaters.

The temperature of water from tankless water heaters shall be a maximum of 140°F (60°C) when intended for domestic uses. This provision shall not supersede the requirement for protective shower valves in accordance with Section 18-29-424.4.

- 18-29-501.6.1  Coils.

Indirect, external, tankless or submerged coils used in heating water shall be equipped with a thermostatic mixing valve or valves when not connected to a storage tank. A pressure relief valve or expansion tank shall be installed on the cold water inlet to the heater. A temperature and pressure relief valve shall be installed on the tempered line with the temperature sensing element immersed in the tempered water pipe as close as possible to the mixing valve.

- 18-29-501.7  Pressure marking of storage tanks.

Storage tanks and water heaters installed for domestic hot water shall have the maximum allowable working pressure clearly and indelibly stamped in the metal or marked on a plate welded thereto or otherwise permanently attached. Such markings shall be in an accessible position outside of the tank so as to make inspection or reinspection readily possible.

- 18-29-501.7.1

Water heaters of 200,000 BTU input per hour or more and storage tanks of 120 gallons (454 L) capacity or more shall be constructed in accordance with ASME Boiler and Pressure Vessel Code, Section IV.

- 18-29-501.8  Temperature controls.

All hot water supply systems shall be equipped with automatic temperature controls capable of adjustments from the lowest to the highest acceptable temperature settings for the intended temperature operating range. Multiple temperature hot water supply systems shall be provided with thermostatic mixing valves to control the desired temperatures.

- 18-29-501.8.1  Instantaneous water heaters.

Direct fired instantaneous water heaters shall be equipped with a thermostatic mixing valve or valves. A pressure relief valve shall be installed on or adjacent to the heater. A temperature and pressure relief valve shall be installed on the tempered line with the temperature sensing element immersed in the tempered water pipe as close as possible to the mixing valve.

- 18-29-501.9  Heat exchangers.

Heat exchangers using a toxic transfer fluid or having conditioning chemicals in the system shall be separated from the potable water by double wall construction. There shall be an air gap open to the atmosphere between the two walls. No heat exchanger will be permitted on any boiler system operating in excess of 65 psi (448.2 kPa), or high temperature hot water system operating in excess of 250°F (121°C), or any steam boiler operating with a pressure in excess of 50 psi (344.75 kPa), unless:

1.     The heat exchanger is double-walled;

2.     The heat exchanger has an air gap open to the atmosphere between the two walls; and

3.     The heat exchanger has a pressure gradient monitor system with a “fail-safe to off” switch installed to isolate the heat exchanger from the potable cold or hot water system. If pressure on the potable water side reaches less than 20 psi (137.9 kPa) above the pressure of the transfer fluid or steam, and a pressure reducing valve is installed on the inlet to the heat exchanger with a setting of 20 psi (137.9 kPa) lower than the potable water pressure at the heat exchanger, an audible alarm shall be activated and the heat exchanger shall be automatically shut off until the alarm and the heat exchanger can be reset manually. Any boiler using toxic chemicals shall have a label with a minimum size of 5 inches by 5 inches (125 mm by 125 mm) attached to the boiler in a conspicuous place. The label shall read as follows:

WARNING Chemicals and additives used to treat the boiler feed water in this boiler are not approved for potable water. The steam or hot water produced by this boiler is not potable. If the steam or hot water produced by this boiler is used to heat water, the water will not be considered potable if the steam and potable water are mixed..

- 18-29-502  Installation.

- 18-29-502.1  General.

Water heaters shall be installed in accordance with the manufacturer's installation instructions. Gas and oil-fired water heaters shall conform to the requirements of this chapter and the mechanical chapter. See mechanical chapters for venting requirements of gas or oil burning appliances. Electric water heaters shall conform to the requirements of this chapter and the provisions of NFPA 70 listed in Article 18-29-14.

- 18-29-502.2  Water heaters installed in non-private garages.

No direct fired water heater shall be installed in any non-private garage (occupancy class H-3, in accordance with Chapter 13-56).

- 18-29-502.3  Rooms used as a plenum.

Water heaters using solid, liquid or gas fuel shall not be installed in a room containing air-handling machinery when such room is used as a plenum.

- 18-29-502.4  Prohibited location.

Fuel-fired water heaters shall not be installed in any of the following locations: a sleeping room; a bathroom; an attic space; a garage or above any ceiling.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-502.5  Water heaters installed in closets accessed through sleeping rooms or bathrooms.

Water heaters may be installed in closets located in sleeping rooms or bedrooms provided that the closet is equipped with a weather-stripped, self-closing, solid door and all air for combustion and dilution is obtained from the outdoors.

- 18-29-502.6  Water heaters installed in attics, basements or other areas.

Areas containing a water heater shall be provided with an opening and unobstructed passageway large enough to allow removal of the water heater. The passageway shall not be less than 30 inches (762 mm) high and 22 inches (559 mm) wide and not more than 20 feet (6.1 m) in length when measured along the centerline of the passageway from the opening to the water heater. The passageway shall have continuous solid flooring not less than 24 inches (610 mm) wide. A level service space at least 30 inches (762 mm) deep and 30 inches (762 mm) wide shall be present at the front or service side of the water heater. The clear access opening dimensions shall be a minimum of 20 inches by 30 inches (508 mm by 762 mm) where such dimensions are large enough to allow removal of the water heater.

- 18-29-503  Connections.

- 18-29-503.1  Cold water line valve.

The cold water branch line from the main water supply line to each hot water storage tank or water heater shall be provided with a valve accessible on the same floor, located near the equipment and only serving the hot water storage tank or water heater. The valving shall not interfere or cause a disruption of the cold water supply to the remainder of the cold water system.

- 18-29-503.1.1  Shutoff valves.

Shutoff valves for water heaters or heated water storage tanks may be installed on the inlet side only. This discharge side may be provided with a check valve or a three-way valve installed to open the heater to the atmosphere when it is not in the operating position. The atmospheric opening of a three-way valve shall be indirectly connected to the drainage system.

- 18-29-503.2  Deliberately omitted.

- 18-29-504  Safety Devices.

- 18-29-504.1  Antisiphon devices.

An approved means shall be provided to prevent siphoning of any storage water heater or tank. A cold water “dip” tube with a hole at the top or a vacuum relief valve installed in the cold water supply line above the top of the heater or tank shall be approved for this purpose. Such a device shall be installed on any water heater or heated water storage tank that supplies a water outlet below the level of the heater.

- 18-29-504.2  Vacuum relief valve.

Water heaters elevated above the fixtures they serve and tanks connected to such water heaters shall have a vacuum relief valve installed. The vacuum relief valve shall comply with ANSI Z21.22.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-504.3  Energy cutoff device.

All automatically controlled water heaters shall be equipped with an energy cutoff device that will cut off the supply of heat energy to the water tank before the temperature of the water in the tank exceeds 200°F (93.3°C). This cutoff device shall be required in addition to the temperature and pressure relief valves.

- 18-29-504.4  Shutdown.

A separate switch shall be provided to terminate the energy supplied to electric hot water supply systems. A separate valve shall be provided to turn off the energy supplied to the main burner of all other types of hot water supply systems.

- 18-29-504.5  Relief valve.

All storage water heaters operating above atmospheric pressure shall be provided with an approved, self-closing (levered) pressure relief valve and temperature relief valve or combination thereof. The relief valve shall conform to ANSI Z21.22. The relief valve shall not be used as a means of controlling thermal expansion.

- 18-29-504.5.1  Installation.

Relief valves shall be installed in the shell of the water heater tank. Temperature relief valves shall be so located in the tank as to be activated by the water in the top 6 inches (150 mm) of the tank served. For installations with separate storage tanks, the valves shall be installed on the tank and there shall not be any type of valve installed between the water heater and the storage tank. There shall not be a check valve or shutoff valve between a relief valve and the heater or tank served.

- 18-29-504.6  Relief valve approval.

Temperature and pressure relief valves (or combinations thereof) and energy cutoff devices shall bear the label of an approved agency and shall have a temperature setting of not more than 200°F (93.3°C) and a pressure setting not exceeding the tank or water heater manufacturer's rated working pressure. Where a pressure rating of more than 150 psi (1034.25 kPa) is not necessary for the proper function of the domestic hot water system, the pressure rating of the relief valve shall be limited to 150 psi (1034.25 kPa). The relieving capacity of each pressure relief valve and each temperature relief valve shall equal or exceed the heat input to the water heater or storage tank, and shall have the AGA steam temperature rating clearly indicated.

- 18-29-504.7  Relief outlet waste.*

The outlet of a pressure, temperature or other relief valve shall not be directly connected to the drainage system.

* Editor's note – Coun. J. 3-28-01, p. 55444, § 1, numbered this section as 18-29-204.7; corrected at the discretion of the editor.

- 18-29-504.7.1  Discharge.

The discharge from the relief valve shall be piped separately to an indirect waste receptor located inside the building. The discharge shall be piped full size and installed in a manner that does not cause personal injury or property damage and that is readily observable by the building occupants. The discharge from a relief valve shall not be trapped. The diameter of the discharge piping shall not be less than the diameter of the relief valve outlet. The discharge pipe shall be installed so as to drain by gravity flow and shall terminate atmospherically not more than 6 inches (150 mm) above the floor. The end of the discharge pipe shall not be threaded.

- 18-29-504.7.2  Location.

The relief outlet discharge piping shall be installed so that it does not leave the room or enclosure in which the water heater and relief valve are located.

- 18-29-504.7.3  Materials.

Relief valve discharge piping shall be of those materials listed in Section 18-29-605.5 for water distribution piping or shall be tested, rated and approved for such use in accordance with ASME A112.4.1. Piping from safety pan drains shall be of those materials listed in Table 18-29-605.5.

- 18-29-504.8  Required pan.

Water heaters or hot water storage tanks installed in locations where leakage of the tanks or connections will cause damage shall be installed in a galvanized steel or other metal pan of equal corrosion resistance having a minimum thickness of 24 gauge, 0.0276 inch (0.70 mm) Any water heater installed in a cabinet below a counter shall be provided with a drain pan.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-504.8.1  Pan size and drain.

The pan shall not be less than 1 1/2 inches (40 mm) deep and shall be of sufficient size and shape to receive all dripping or condensate from the tank or water heater. The pan shall be drained by an indirect waste pipe having a minimum diameter of 1 inch (25 mm) or the outlet diameter of the required relief valve, whichever is larger.

- 18-29-504.8.2  Pan drain termination.

The pan drain shall extend full-size and terminate over a suitably located indirect waste receptor or floor drain.

- 18-29-505  Insulation.

- 18-29-505.1  Unfired vessel insulation.

Unfired hot water storage tanks shall be insulated so that heat loss is limited to a maximum of 15 British thermal units per hour (Btu/h) per square foot (47 W/m2) of external tank surface area. For purposes of determining this heat loss, the design ambient temperature shall not be higher than 65°F (18.3°C). Any ASME stamp or other required indication markings shall remain exposed.

- Article 6.  Water Supply and Distribution

- 18-29-601  General.

- 18-29-601.1  Scope.

This article shall govern the materials, design and installation of water supply systems, both hot and cold, for utilization in connection with human occupancy and habitation and shall govern the installation of individual water supply systems. In any building or structure in the city of Chicago, any water pipe or pipes or systems of water piping which receives or is intended to receive, its service from the Chicago Waterworks System shall be administered and enforced by the commissioner of the department of water. In all premises supplied with water from the Chicago Water Works System, the owner, agent, lessee, or occupant shall maintain in good condition all plumbing fixtures and appurtenances, service pipes including meter connections, and water supply piping from the curb valve to the further-most water outlet.

- 18-29-601.2  Inspections and notices.

It shall be the duty of the commissioner of water to inspect the installation of, extension to, or any alterations in all water service, water supply or water distribution piping system in all buildings, structures, and premises having service from the Chicago Water Works System.

The officers and employees of the department of water or anyone authorized to act for it, shall have free entry and access to any building, structure or premise or part thereof, whether completed or in the process of erection, for the purpose of determining whether the building provisions of this code are complied with, and wherever it is found that such installation, extension, or alteration does not conform, it shall be his duty to serve written notice on owner, occupant or person in possession of such building, structure or premise of non- compliance to make such alterations or repairs as are necessary to eliminate the cause or causes of nonconformity, and in case of failure to do so within 10 days from the date of such notice, the commissioner of water may cause the water supply from the Chicago Water Works System to be shut off until the requirements in the building provisions of this code are complied with. Nothing herein contained shall be deemed to apply to any building, structure or premise existing on August 3, 1938, unless the plumbing or water distribution system in said existing buildings are changed in a degree exceeding “minor repairs” as defined in Section 18-29-202 of this Code or where conditions hazardous to health exist due to connections to the city water supply in violation of this code.

- 18-29-601.3  Access for inspections.

The department of water and any person delegated or authorized by the commissioner of water shall have free entry and access to every part of any building, structure or premises whenever such entry or access is deemed necessary or advisable. Wherever any person, in possession, charge or control of any such building structure, or premises, into which any officer or authorized person shall desire entry or access, shall refuse to permit such entry or access, the commissioner of water may turn off the water service from said building, structure or premises, until notice shall have given* the commissioner in writing that entry or access will be permitted or provided and until such entry or access shall have been accomplished.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “...have been given....”

- 18-29-601.4  Solar energy utilization.

Solar energy systems used for heating potable water or using an independent medium for heating potable water shall comply with the applicable requirements of this Article. The use of solar energy shall not compromise the requirements for cross connection or protection of the potable water supply system required by this chapter.

- 18-29-602  Water Required.

- 18-29-602.1  General.

Every structure equipped with plumbing fixtures and utilized for human occupancy or habitation shall be provided with a potable supply of water from the Chicago Waterworks System at the rates and charges specified in Chapter 11-12, in the amounts and pressures specified in this article.

- 18-29-602.1.1  Obligations of water consumers.

Every person who shall construct, enter, alter, or use any part of the Chicago Water Works System and every consumer of water and owner, occupant, or person in possession, charge or control of any building, structure, or premises having service therefrom, shall be governed by and subject to the provisions of this code governing the use of water and also such other rules and regulations governing the use of water as may from time to time be promulgated by the commissioner of water. It is hereby made the duty of the commissioner of water to enforce the provisions of this code governing the use of water, and also any rules and regulations that may be promulgated as aforesaid.

- 18-29-602.2  Potable water required.

Only potable water shall be supplied to plumbing fixtures that provide water for drinking, bathing or culinary purposes, or for the processing of food, medical or pharmaceutical products. Unless otherwise provided in this Article, potable water shall be supplied to all plumbing fixtures.

- 18-29-602.3  Deliberately omitted.

- 18-29-602.4  Reserve water supply.

Whenever a continuous supply of water is deemed indispensable by the Commissioner of Water, or Fire Commissioner, the owner or occupant shall provide a tank (or other receptacle of sufficient capacity) to supply the needs of such building including any required fire protection, structure or premises, including any required for fire protection, during the period that the pipe section to which the service pipe is connected is shut off for repairs, connections, extensions or testing purposes.

- 18-29-602.4.1  Installation of line valves or taps.

In lieu of the installation of such a tank or other receptacle, the owner or occupant shall provide for continuous water supply by requesting the city to install line valves in the water main or to install a tap in the water main for an auxiliary or emergency connection of a second service pipe with separate meter control so that each service pipe shall have an independent source of supply.

- 18-29-602.4.2  Dual meter settings.

To further insure a continuous supply of water where line valves are installed in the water main, dual meter settings shall be installed by the owner or occupant. The cost of these installations is to be borne by the owner or occupant of the building, structure or premises to which the water service is furnished.

- 18-29-603  Water Service.

- 18-29-603.1  Size of water service pipe.

The service pipe is the pipe which conveys the water from the mains of the Chicago Waterworks System to the building, structure, or premises served. Each service pipe shall be of sufficient size to permit the continuous and ample flow of water to supply adequately all floors at any given time. No service pipe of a nominal pipe size less than 1 inch (25 mm) shall be installed in any public way or other public place of the city, nor connected to the mains of the Chicago Waterworks System.

- 18-29-603.1.1  Size and meter spreader connection.

Service pipes shall be sized according to the formula prescribed in Section 18-29-604.10.1, plus any additional requirements for fire protection purposes. Each service pipe shall include a meter spreader connection of like size and of sufficient length to accommodate a full-size meter.

- 18-29-603.1.2  Sizing of connections.

City connection shall be increased 2 inches where used to serve domestic and fire protection demands when the domestic exceeds 2 inches.

- 18-29-603.1.2  Increased connection required.*

City connection shall be increased by 2 inches where used to serve both domestic and fire protection demands when the domestic exceeds 2 inches.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; section numbering and text duplicate that of the immediately preceding section, sizing of connections.

- 18-29-603.1.3  Permits to install water supply in buildings.

Application. No person shall install in any building or structure in the city any pipe or pipes or systems of piping which receives its service from the Chicago Waterworks System, nor shall make any alterations in, or additions or extensions to, any structure which was erected previous to August 3, 1938, until such person shall have made application to the department of water for permission for such installation, alteration, addition, or extension; provided, however, that wherever such installation or construction work is done, wherever an emergency exists for the purpose of preventing the loss or damage to property, such application may be dispensed with.

Application in Writing. All applications for permits for the installation in any building or structure, of water supply or water distribution pipes, or systems of piping, shall be in writing upon printed forms furnished by the department of water.

Service Shut Off Until Permit Issued. The commissioner of water may withhold or shut off service from any building, structure, or premises, or to any portion thereof, in which shall be found any plumbing work, fixture, or any apparatus which has not been installed in accordance with the provisions of this chapter, until such plumbing work, fixture, or apparatus has been disconnected or until a proper permit has been issued.

- 18-29-603.2  Separation of water service and building sewer/drain.

All service pipes in public ways or other places exposed to the weather shall be installed at a depth of not less than 60 inches (1525 mm) below the surface of the ground or pavement and at right angles to the main to which they are connected.

- 18-29-603.2.1  Individual trench.

Each service pipe shall be installed in a separate individual trench. Such trench shall be not less than 72 inches (1830 mm) distance from any other trench or excavation of greater depth than that in which service pipe is laid, except in public ways where permanent pavement exists.

- 18-29-603.2.2  Permanent pavement.

Where permanent pavement exists, service may be laid on a solid earthen shelf not less than 1 foot (300 mm) from a trench in which a house sewer or other parallel conduit is installed, provided that a service pipe may cross at right angles any trench which may be excavated on a line parallel with the centerline of the public way in which the service pipe is installed.

- 18-29-603.2.3  Backfill.

No ashes, cinders or refuse shall be used in backfllling any trench or excavation in which service pipes are installed. Each service pipe trench from the water main to the property line shall be filled with sand and compacted by flooding with water. When a service pipe is to be installed in soil which may have a destructive or deleterious effect it must be protected by methods approved by the department of water.

Exception: The required separation distance shall not apply where the bottom of the water service pipe within 60 inches (1524 mm) of the sewer is a minimum of 12 inches (300 mm) above the top of the highest point of the sewer and the pipe materials conform to Section 18-29-703.1.

- 18-29-603.3  Metered service.

No building, structure, or premises shall be allowed to have service from the Chicago Waterworks System until an application in writing has been made to the commissioner of water by the person desiring such service, and until said commissioner has given permission.

- 18-29-603.3.1  Authority.

Where application has been made for permission to connect at the main for water service for any projected building or structure, or for any alteration or addition in any building or structure, which from the information given in such application, would appear to come under any provision of this Article, said permit shall be authority to install metered service only.

- 18-29-603.3.2  Connection of nonmetered to metered service.

Where this chapter requires the water supply for any building, structure, premises, or any part thereof to be under meter control, it shall be unlawful for any person to connect any building, structure, or premises, or any part thereof or addition thereto, with any service or supply pipe other than a service or supply controlled by meter.

- 18-29-603.3.3  Licensed and bonded contractor.

Where this chapter or the rules or regulations of the department of water provide for the installation of a water meter on any service pipe supplying water from the Chicago Waterworks System to any building, structure, or premises, such meter shall be installed by a licensed and bonded plumbing contractor.

- 18-29-603.3.4  Location.

The location of such meter, either inside or outside of any building or structure, shall be determined by the water commissioner. The installation of any water meter at any location other than that determined by the said commissioner is prohibited. Installation of any water meter shall be in accordance with the following locations:

1.     No meter may be installed in the living quarters of a building.

2.     For services 1 inch (25 mm), 1 1/2 inches (40 mm) or 2 inches (50 mm) diameter: Meters shall be installed within 2 feet (610 mm) of the front wall of the building. The maximum distance a meter may be installed from the property line to meter is 50 feet (15.25 m). Any installation of a service 1 inch (25 mm), 1 1/2 inches (40 mm) and 2 inches (50 mm) over 50 feet (15.25 m) will require the installation of a meter vault in the public way.

3.     For services 3 inches (75 mm) diameter and above: Meters shall be installed within 4 feet (1220 mm) of the front wall of the building. The maximum distance the meters may be installed from property line is 100 feet (30.5 m). A meter vault is required in the public way in any circumstance in which the distance from the property line to the meters exceeds 100 feet (30.5 m). Any installation in excess of 100 feet (30.5 m) will require the installation of a meter vault in the public way.

4.     All new combination (fire and domestic) service shall require a domestic meter and an approved backflow device with bypass meter for the fire system. If these services are in excess of the 50' for 2 inches (15.25 m:50 mm) or 100"* for 3 inches (30.5 m:75 mm) they must meet the above requirement and shall require the backflow preventer to be installed in an above ground-heated enclosure “hot box,” located as close to the property line as physically possible.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct measurement appears to be 100'.

5.     Service used in conjunction with trunk lines (private water mains) requiring private fire hydrants shall have compound meters installed in a meter vault in the public way. Private hydrants are to be painted federal safety green, annually inspected and tested by the commissioner of fire. Results and inspection reports are to be filed with the department of water within 30 days of inspection or test.

- 18-29-603.3.5  Construction of meter vaults.

Wherever water meter is installed in the ground, either inside or outside of any building or structure on public or privately owned property, it shall be enclosed in a meter vault. Such vault shall be built of hard pressed common brick or portland cement concrete blocks laid up in portland cement mortar, poured portland cement concrete, extra heavy, salt-glazed vitrified clay tile pipe, portland cement concrete pipe, or equally durable material. This meter vault shall be provided with a cast iron cover frame and removable cast iron cover. Each meter vault shall be built to conform to the specifications and dimensions for meter vaults on file at the offices of the department of water.

- 18-29-603.3.6  Installation of taps.

No water main shall be tapped other than by a tapper employed by the department of water, and all tapping shall be performed only under the authority of the commissioner of water. All service cocks or ferrules must be inserted at or near the top of the street main, and not nearer than 6 inches (150 mm) from the bell of the pipe. The size of the cock shall be that specified in the permit. Each service pipe shall have its own independent tap at the main and said tap shall be of the type in use by the department of water.

- 18-29-603.3.7  Plans accompany permit application.

No permit for the installation of any pipe or system of piping taking water from the Chicago Waterworks System for distribution in any building or structure shall be granted until plan of such water supply or distribution system has been examined and approved by the department of water. Such plan or plans shall be presented with the application for permit to the department of water in duplicate, and shall clearly show the complete water supply piping system from the service to the plumbing fixtures and other appliances including fire protection equipment, to which such water supply piping system is connected, together with detail drawings of connections to surge tanks, storage tanks, pressure tanks, filters, swimming pools, bathing and display pools, hydrotherapy pools, sterilizers, condensers, compressors, reservoirs, and washers. Said plans shall be drawn to a scale of not less than 1/8 inch to the 1 foot; provided, however, that detail plans shall be drawn to 1/4 inch scale and diagrams may be presented in either horizontal and vertical plans or isometric form.

For private water systems within the city of Chicago the owner, agent, contractor or permittee shall provide to the department of water an as built drawing within 30 days of completion of private water system. The as built drawing shall identify the location and size for every main, control valve, meter vault, fire hydrant, line valve, service valve, meter and individual service location connected to the Chicago Water Works System.

- 18-29-603.3.8  Notification of wrecking buildings.

No building, structure, or premises shall be permanently abandoned, wrecked, or destroyed without the previous notification, in writing, to the commissioner of water of such abandonment, wrecking or destroying, in order that the water service may be shut off, and leaking or wasting water shall be eliminated or prevented; and accompanying said notification, ample financial provisions, such as the deposit of the estimated costs of disconnection and sealing of water service pipes or posting of a surety bond, shall be made to the satisfaction of said commissioner of water to ensure the payment of all costs and charges for the shutting off of said water service. Such notification and assurance of payment shall be given by the person in charge of the wrecking or destroying of the building or by the owner of the building, structure, or premises.

No water service pipe shall be permanently sealed by other than an employee of the department of water and all such permanent sealing shall be performed only under the authority of the commissioner of water.

- 18-29-604  Design of Building Water Distribution System.

- 18-29-604.1  General.

The design of the water distribution system shall conform to accepted engineering practice. Methods utilized to determine pipe sizes shall be approved by the commissioner of water.

- 18-29-604.2  System interconnection.

At the points of interconnection between the hot and cold water supply piping systems and the individual fixtures, appliances or devices, provisions shall be made to prevent flow between such piping systems.

- 18-29-604.3  Water distribution system design criteria.

The water distribution system shall be designed, and pipe sizes shall be selected such that under conditions of peak demand, the capacities at the fixture supply pipe outlets shall not be less than shown in Table 18-29-604.3.

Table 18-29-604.3
Water Distribution System Design Criteria Required Capacities at Fixture Supply Pipe Outlets

Fixture Supply Outlet Serving; Flow Rate a; Flow Pressure (psi). Bathtub; 4; 8. Bidet; 2; 4. Combination fixture; 4; 8. Dishwasher, residential; 2.75; 8. Drinking fountain; 0.75; 8. Laundry tray; 4; 8. Lavatory; 2; 8. Shower; 3; 8. Shower, temperature controlled; 3; 20. Silkock, hose bibb; 5; 8. Sink, residential; 2.5; 8. Sink, service; 3; 20. Urinal, valve; 15; 20. Water closet, blow out, flushometer valve; 35; 25. Water closet, flushometer tank; 1.6; 20. Water closet, siphonic, flushometer valve; 25; 25. Water closet, tank, close coupled; 3; 8. Water closet, tank, one piece; 6; 20. Water closet, tank, pressure assist; 3; 25.

For SI: 1 psi = 67.895 kPa, 1 gallon per minute (gpm) = 3.785 L/m.

a For additional requirements for flow rates and quantities, see 18-29-604.4.

- 18-29-604.4  Maximum flow and water consumption.

The maximum water consumption flow rates and quantities for all plumbing fixtures and fixture fittings shall be in accordance with Table 18-29-604.4. Water consumption for urinals listed in the following exceptions shall not be greater than 1.5 gallons (5.7 L) per flushing cycle.

Exceptions:

1.     Blowout design fixtures.

2.     Penalware.

3.     Clinical sinks.

4.     Service sinks.

5.     Emergency showers.

Table 18-29-604.4
Maximum Flow Rates and Consumption for Plumbing Fixtures and Fixture Fittings

Plumbing Fixture or Fixture Fitting; Maximum Flow Rate or Quantity a. Lavatory, private; 2.5 gpm at 80 psi. Lavatory, public; 0.5 gpm at 80 psi. Lavatory, public, metering or self-closing; 0.5 gallons per metering cycle. Shower head; 2.5 gpm at 80 psi. Sink faucet; 2.5 gpm at 60 psi. Urinal; 1.0 gallons per flushing cycle. Water closet; 1.6 gallons per flushing cycle.

For SI: 1 gallon = 3.785 L, 1 gpm = 3.785 L/m, 1 psi = 6.895 kPa

a Consumption tolerances shall be determined from referenced standards

- 18-29-604.4.1  Deliberately omitted.*

* Editor's note – Coun. J. 3-28-01, p. 55444, § 1, did not provide for a Section 18-29-604.4.1.

- 18-29-604.4.2  Water closets.

Water consumption for water closets listed in the following exceptions shall not be greater than 4 gallons (15 L) per flushing cycle.

Exceptions:

1.     Water closets provided for the public in theaters, nightclubs, restaurant, halls, museums, coliseums, arenas, churches, schools, stadiums and similar occupancies.

2.     Water closets provided for patients and residents in, hospitals, nursing homes, sanitariums and similar occupancies.

3.     Water closets provided for inmates and residents in prisons, asylums, reformatories and similar occupancies.

- 18-29-604.5  Size of fixture supply.

The minimum size of a fixture supply pipe shall be as shown in Table 18-29-604.5. The fixture supply pipe shall not terminate more than 30 inches (762 mm) from the point of connection to the fixture. A reduced-size connector installed between the supply pipe and the fixture shall be of approved type. The supply pipe shall extend to the floor or wall adjacent to the fixture.

Table 18-29-604.5
Minimum Sizes of Fixture Water Supply Pipes

Fixture; Minimum Pipe Size (inch). Bathtubs: 60" by 32" and smaller; 1/2. Bathtubs: Larger than 60" by 32"; 1/2. Bidet; 3/8. Combination sink and tray; 1/2. Dishwashing machine (domestic); 1/2. Drinking fountain; 1/2. Hose bibbs; 3/4. Kitchen sink; 1/2. Domestic; 3/4. Commercial; 3/4. Laundry, 1, 2 or 3 compartments; 1/2. Lavatory; 3/8. Shower, single head; 1/2. Sinks, flushing rim; 3/4. Sinks, service; 3/4. Urinal, flush tank; 1/2. Urinal, flush valve; 1. Wall hydrant; 3/4. Washing machine (automatic); 1/2. Water closet, flush tank; 1/2. Water closet, flush valve; 1. Water closet, flushometer tank; 3/8. Water closet, one piece; 1/2.

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 psi = 6.895 kPa.

- 18-29-604.5.1  Minimum size.

The minimum size of individual distribution lines utilized in parallel water distribution systems shall be as shown in Table 18-29-604.5.

- 18-29-604.6  Variable street pressures.

Where street water main pressures fluctuate, the building water distribution system shall be designed for the minimum pressure available.

- 18-29-604.7  Inadequate water pressure.

Wherever water pressure from the street main or other source of supply is insufficient to provide flow pressures at fixture outlets as required under Section 18-29-604.3, a water pressure booster system conforming to Section 18-29-606.5 shall be installed on the building water supply system.

- 18-29-604.8  Water pressure reducing valve or regulator.

Where water pressure within a building exceeds 100 psi (690 kPa) static at any fixture or outlet, an approved water pressure reducing valve conforming to ASSE 1003 with strainer shall be installed to reduce the pressure at any fixture or outlet in the building water distribution piping to 100 psi (690 kPa) static or less.

- 18-29-604.8.1  Valve design.

The pressure reducing valve shall be designed to remain closed in case of valve failure.

- 18-29-604.8.2  Repair and removal.

All water pressure reducing valves, regulators and strainers shall be so constructed and installed as to permit repair or removal of parts without breaking a pipeline or removing the valve and strainer from the pipeline.

- 18-29-604.9  Deliberately omitted.

- 18-29-604.10  Size of water supply pipes.

Each main supply pipe, principal supply pipe, branch supply pipe, riser pipe, distributing pipe, or branch distributing pipe shall be of a size which under normal pressure shall deliver a full volume of water to each and all of its outlets.

- 18-29-604.10.1  Minimum sizes of branch distributing pipes for fixtures and appliances.

The water supply system shall be designed on the basis of the minimum available pressure at the water main or other source of water supply. The minimum available pressure will be given by the department of water for each location.

- 18-29-604.10.1.1  Demand load.

The water supply demand load in the distributing system shall be based upon the number, type, and probable simultaneous use of the fixtures to be supplied.

- 18-29-604.10.1.2  Size of piping.

The size of piping shall be such that the velocity of each flow during maximum demand will not exceed 8 feet (2440 mm) per second velocity in the main supply pipe, principal supply pipe, and branch supply pipe. When a water service requires a pump, the velocity of flow in the service shall not exceed 5 feet (1525 mm) per second velocity.

- 18-29-604.10.1.3  Available pressure.

In determining the available pressure to overcome friction in the piping system, head meter and other losses shall be deducted from the minimum available pressure source. When the pressure exceeds 100 psi (690 kPa) at any plumbing fixture, the pressure shall be reduced by an approved type reducing valve. The minimum size of fixture supply pipes are shown in Table 18-29-604.5.

- 18-29-604.10.2  Procedures for calculating sizing.

See Appendix A for procedures for sizing of the water supply system.

- 18-29-604.11  Air chambers required.

Air chambers shall be installed at the upper terminals of all upfeed riser pipes and in branch distributing pipes contiguous to, and directly above, the connection of such branch distributing pipes to the plumbing fixture or other water-supplied appliance. Such air chambers shall be installed in a direct line with the flow of water through such pipes and shall be of sufficient capacity to provide an air cushion which will absorb shock, stress, or strain or eliminate all excess noises which may be caused by the operation of any valves, faucets, bibbs, or cocks in the water supply system.

- 18-29-604.11.1  Size of air chamber.

No air chamber which is constructed of pipe shall be of a size less than the pipe which it serves and to which it is connected and shall be not less than 2 feet (610 mm) in length. The air chamber on each water supply branch connection to a plumbing fixture shall be not less than 12 inches (300 mm) long.

- 18-29-605  Materials, Joints and Connections.

- 18-29-605.1  Water compatibility.

Water service pipe and water distribution pipe shall be resistant to corrosive action and degrading action from the potable water supplied by the water purveyor or individual water supply system.

- 18-29-605.2  Soil and ground water.

The installation of a water service pipe shall be prohibited in soil and ground water contaminated with solvents, fuels, organic compounds or other detrimental materials causing permeation, corrosion, degradation or structural failure of the piping material. Where detrimental conditions are suspected, a chemical analysis of the soil and ground water conditions shall be required to ascertain the acceptability of the water service material for the specific installation. Where detrimental conditions exist, approved alternative materials or routing shall be required.

- 18-29-605.3  Lead content of water supply pipe and fittings.

Pipe and pipe fittings (including valves and faucets) utilized in the water supply system shall have a maximum of 8 percent lead content.

- 18-29-605.4  Water service pipe.

Water service pipe shall conform to NSF 61 and to one of the standards listed in Table 18-29-605.4. All water service pipe or tubing, installed underground and outside of the structure, shall have a minimum working pressure rating of 160 psi (1100 kPa) at 73.45°F (23.03°C). Where the water pressure exceeds 160 psi (1100 kPa), piping material shall have a minimum rated working pressure equal to the highest available pressure. All ductile iron water pipe shall be cement mortar lined in accordance with AWWA C104.

Table 18-29-605.4
Water Service Pipe

Material; Standard. Copper or copper-alloy tubing (Type K); ASTM B 75; ASTM B 88; ASTM B 251; ASTM B 447. Ductile iron water pipe; AWWA C151; AWWA C115.

- 18-29-605.4.1  Materials for supply pipes and fittings.

All new and replaced water supply pipes and fittings shall be of materials specified in Tables 18-29-605.4, 18-29-605.5 and 18-29-605.6, subject to the restrictions indicated in Column B of the table. Water supply pipe and fittings shall conform to the standards cited in Tables 18-29-605.4, 18-29-605.5 and 18-29-605.6. All pipe and fittings exceeding 8 percent lead content are prohibited in the installation, repair or replacement of water supply pipes.

- 18-29-605.5  Water distribution pipe.

Water distribution pipe shall conform to NSF 61 and shall conform to one of the standards listed in Table 18-29-605.5. All hot water distribution pipe and tubing shall have a minimum pressure rating of 100 psi (690 kPa) at 1805°F (825°C).

Table 18-29-605.5
Water Distribution Pipe

Material; Standard. Brass pipe; ASTM B 43. Chlorinated Polyvinyl Chloride (CPVC) plastic pipe and tubing a; ASTM D 2846; ASTM F 441; ASTM F 442; CSA B 137.6. Polypropylene (PP) plastic pipe and tubing a; ASTM F 1412. PVDF plastic pipe and tubing a; ASTM F 1412. Copper or copper-alloy pipe; ASTM B 42; ASTM B 302. Copper or copper-alloy tubing (Type K, L, or M); ASTM B 74; ASTM B 88; ASTM B 251; ASTM B 447. Galvanized steel pipe; ASTM A 53.

a For secondary water used in process applications only.

- 18-29-605.6  Fittings.

Pipe fittings shall be approved for installation with the piping material installed and shall conform to the respective pipe standards or one of the standards listed in Table 18-29-605.6. All pipe fittings utilized in water supply systems shall also conform to NSF 61. The fittings shall not have ledges, shoulders or reductions capable of retarding or obstructing flow in the piping. Ductile and gray iron pipe fittings shall be cement mortar lined in accordance with AWWA C104.

Table 18-29-605.6
Pipe Fittings

Material; Standard. Cast iron; ASME B 16.4; ASME B 16.12. Polypropylene (PP) plastic pipe and tubing a; ASTM F 1412. PVDF plastic pipe and tubing a; ASTM F 1412. Chlorinated polyvinyl chloride (CPVC) plastic a; ASTM F 437; ASTM F 438; ASTM F 439. Copper or copper alloy; ASME B 16.15; ASME B 16.18; ASME B 16.22; ASME B 16.23; ASME B 16.26; ASME B 16.29; ASME B 16.32. Gray iron and ductile iron; AWWA C 110; AWWA C 153. Malleable iron; ASME B 16.3. Steel; ASME B 16.9; ASME B 16.11; ASME B 16.28.

a For secondary water used in process applications only.

- 18-29-605.7  Valves.

All valves shall be compatible with the type of piping material installed in the system.

- 18-29-605.8  Manufactured pipe nipples.

Manufactured pipe nipples shall conform to the following standards:

1)     Steel nipples: ASTM A 733.

2)     Brass-plated, copper-plated, or nickel-plated: ASTM B 687

- 18-29-605.9  Prohibited joints and connections.

The following types of joints and connections shall be prohibited:

1.     Cement or concrete joints;

2.     Joints made with fittings not approved for the specific installation;

3.     Solvent-cement joints between different types of plastic pipe;

4.     Saddle-type fittings;

5.     Dresser couplings.

- 18-29-605.10  Deliberately omitted.

- 18-29-605.11  Deliberately omitted.

- 18-29-605.12  Brass.

Joints between brass pipe or fittings shall comply with Sections 18-29-605.12 through 18-29-605.12.4.

- 18-29-605.12.1  Brazed joints.

All joint surfaces shall be cleaned. An approved flux shall be applied where required. The joint shall be brazed with a filler metal conforming to AWS A5.8.

- 18-29-605.12.2  Mechanical joints.

Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-605.12.3  Threaded joints.

Threads shall conform to ASME B 1.20.1. Pipe- joint compound or tape shall be applied on the male threads only.

- 18-29-605.12.4  Welded joints.

All joint surfaces shall be cleaned. The joint shall be welded with an approved filler metal.

- 18-29-605.13  Gray iron and ductile iron joints.

Joints for gray and ductile iron pipe and fittings shall comply with AWWA C111 and shall be installed in accordance with the manufacturer's installation instructions.

- 18-29-605.14  Copper pipe.

Joints between copper or copper-alloy pipe or fittings shall comply with Sections 18-29-605.14.1 through 18-29-605.14.3.

- 18-29-605.14.1  Deliberately omitted.

- 18-29-605.14.2  Deliberately omitted.

- 18-29-605.14.3  Soldered joints.

Solder joints shall be made in accordance with the methods of ASTM B 828. All cut tube ends shall be reamed to the full inside diameter of the tube end. All joint surfaces shall be cleaned. A flux conforming to ASTM B 813 shall be applied. The joint shall be soldered with a solder conforming to ASTM B 32. The joining of water supply piping shall be made with lead- free solder and fluxes. “Lead free” shall mean a chemical composition equal to or less than 0.2 percent lead.

- 18-29-605.15  Copper tubing.

Joints between copper or copper-alloy tubing or fittings shall comply with Sections 18-29-605.15.1 through 18-29-605.15.4.

- 18-29-605.15.1  Brazed joints.

All joint surfaces shall be cleaned. An approved flux shall be applied where required. The joint shall be brazed with a filler metal conforming to AWS A5.8.

- 18-29-605.15.2  Flared joints.

Flared joints for water pipe shall be made by a tool designed for that operation.

- 18-29-605.15.3  Mechanical joints.

Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-605.15.4  Soldered joints.

Solder joints shall be made in accordance with the methods of ASTM B 828. All cut tube ends shall be reamed to the full inside diameter of the tube end. All joint surfaces shall be cleaned. A flux conforming to ASTM B 813 shall be applied. The joint shall be soldered with a solder conforming to ASTM B 32. The joining of water supply piping shall be made with lead- free solders and fluxes. “Lead free” shall mean a chemical composition equal to or less than 0.2 percent lead.

- 18-29-605.16  CPVC plastic.

Joints between CPVC plastic pipe or fittings shall comply with Sections 18-29-605.16.1 through 18-29-605.16.3 (For use on secondary water piping in process applications only).

- 18-29-605.16.1  Mechanical joints.

Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-605.16.2  Solvent cementing.

Joint surfaces shall be clean and free from moisture and an approved primer shall be applied. Solvent cement, orange in color and conforming to ASTM F 493, shall be applied to all joint surfaces. The joint shall be made while the cement is wet, and in accordance with ASTM D 2846 or ASTM F 493. Solvent-cement joints shall be permitted above or below ground.

- 18-29-605.16.3  Threaded joints.

Threads shall conform to ASME B 1.20.1. Schedule 80 or heavier pipe shall be permitted to be threaded with dies specifically designed for plastic pipe, but the pressure rating of the pipe shall be reduced by 50 percent. Thread by socket molded fittings shall be permitted. Approved thread lubricant or tape shall be applied on the male threads only.

- 18-29-605.17  Steel.

Joints between galvanized steel pipe or fittings shall comply with Sections 18-29-605.17.1 and 18-29-605.17.2.

- 18-29-605.17.1  Threaded joints.

Threads shall conform to ASME B 1.20.1. Pipe- joint compound or tape shall be applied on the male threads only.

- 18-29-605.17.2  Mechanical joints.

Joints shall be made with an approved elastomeric seal. Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-605.18  Deliberately omitted.

- 18-29-605.19  Deliberately omitted.

- 18-29-605.20  Deliberately omitted.

- 18-29-605.21  Joints between different materials.

Joints between different piping materials shall be made with a mechanical joint of the compression or mechanical-sealing type, or as permitted in Section 18-29-605.21.1.

- 18-29-605.21.1  Copper or copper-alloy tubing to galvanized steel pipe.

Joints between copper or copper-alloy tubing and galvanized steel pipe shall be made with a brass converter fitting or dielectric fitting. The copper tubing shall be soldered to the fitting in an approved manner, and the fitting shall be screwed to the threaded pipe.

- 18-29-605.22  Protection for pipes and fixtures.

All new concealed water pipes, storage tanks, flushing services or systems and all pipes or tanks exposed to low temperatures shall be protected from freezing.

- 18-29-605.23  Hydrants and non-freeze hydrants protection.

Every hydrant providing drinking water shall be protected from surface water and ground contamination.

- 18-29-605.24  Water supply pipe protection.

All water supply pipes or distributing pipes that are installed in the ground in any public way or other public place or in buildings, structures, or privately owned premises shall be covered to a minimum depth of not less than 5 feet (1525 mm) below the surface of the ground. No ashes, cinders, or refuse shall be used in back-filling any trenches or excavations in which water pipes are installed. All such pipes shall be coated with coal tar paint and insulated where they pass through concrete floors, or new concrete or masonry walls.

- 18-29-605.25  Refrigerant condensers.

No refrigerant condenser of the water jacket type with a common wall between the refrigerant gas and the cooling water shall be directly connected to the city water supply. Cooling water, if from the city water supply, shall be obtained by gravity through an indirect connection. If water under pressure is required, it may be supplied only by means of a reduced pressure backflow preventer.

- 18-29-605.26  Dead-ends prohibited.

Unused sections of water supply piping systems (or so called dead-ends) where city water will become stagnant are prohibited other than fire protection systems protected and installed in accordance with Table 18-29-608.1.

- 18-29-605.27  Air conditioning and refrigeration systems.

All new or newly remodeled refrigeration systems employing water from the city mains for condensing purposes in the process of providing space air conditioning for commercial, industrial or residential use shall be closed air conditioning systems employing recirculation of cooling water to conserve water.

- 18-29-605.28  Permissible exceptions.

Any and all exceptions to this provision will be permitted only by action of the commissioner of water.

- 18-29-606  Installation of the Building Water Distribution System.

- 18-29-606.1  Location of full-open valves.

Full-open valves shall be installed in the following locations:

1.     On the building water service pipe from the public water supply near the curb;

2.     On the water distribution supply pipe at the entrance into the structure;

3.     On the discharge side of every water meter;

4.     On the base of every water riser pipe in occupancies other than multiple family residential occupancies that are two stories or less in height and in one- and two-family residential occupancies etc.;

5.     On the top of every water down-feed pipe in occupancies other than one- and two-family residential occupancies;

6.     On the entrance to every water supply pipe to a dwelling unit, except where supplying a single fixture equipped with individual stops;

7.     On the water supply pipe to a gravity or pressurized water tank;

8.     On the water supply pipe to every water heater.

- 18-29-606.2  Location of shutoff valves.

Shutoff valves shall be installed in the following locations:

1.     On the fixture supply to each plumbing fixture except one- and two-family or multiple family residential occupancies, or individual guestrooms that are provided with unit shutoff valves in hotels, motels, boarding houses and similar occupancies;

2.     On the water supply pipe to each sillcock;

3.     On the water supply pipe to each appliance or mechanical equipment; and

4.     On water services 1 1/2 inches (40 mm) or larger requiring meters either in the building or in a meter vault, valves shall be installed on the inlet and outlet sides of the meter and as near as practicable thereto. Meters on 1-inch (25 mm) services have a valve on the inlet side only. Valves located in the meter vault shall not eliminate the need for the valve in the building. All such valves shall be accessible for operation at all times.

- 18-29-606.3  Access to valves.

Access shall be provided to all required full-open valves and shutoff valves.

- 18-29-606.4  Valve identification.

Service and hose bibb valves shall be identified. All other valves installed in locations that are not adjacent to the fixture or appliance shall be identified, indicating the fixture or appliance served.

- 18-29-606.5  Water pressure booster systems.

Water pressure booster systems shall be provided as required by Sections 18-29-606.5.1 through 18-29-606.5.10.

- 18-29-606.5.1  Hydropneumatic system, booster pump system, gravity tank.

When the water pressure in the city water main is insufficient to furnish an adequate water supply for any purpose in any building, structure or premises, a hydropneumatic system, booster pump system, or gravity tank shall be installed.

- 18-29-606.5.1.1  Requirements.

All hydropneumatic systems shall consist of a water pump or pumps and a pressure tank and shall be provided with controls to insure complete automatic operation. The material and construction of the tank shall be in accordance with the ASME Rules for the Construction of Unfired Pressure Vessels, Section VIII dated 1973.

- 18-29-606.5.1.1.1  Pressure relief valve.

Each pump serving such tanks shall have a pressure relief valve on the discharge side capable of relieving water pressure in excess of the designed working pressure of such tanks.

- 18-29-606.5.1.1.2  Compression tank.

Each compression tank shall be so connected that the air content thereof shall be no less than 25 percent of its total capacity. Each compression tank shall be provided with a sludge drain pipe which shall be connected to such tank at the lowest level of the bottom section thereof and shall discharge through an indirect connection into the drainage system with a minimum air gap of 6 inches (150 mm).

- 18-29-606.5.1.1.3  Sludge drain pipe.

Each sludge drain pipe shall be equal in size to the inlet pipe but need not exceed 2 inches (50 mm) and shall be provided with a control valve having a clear waterway equal in area to that of the sludge drain pipe.

- 18-29-606.5.1.2  Booster pump system.

Booster pump systems may be of the constant speed type or the variable frequency drive type. Each pump or pumps shall have sufficient capacity to furnish an adequate supply of water for any purpose. When one pump is installed it shall run continuously or when a multipump system is installed the lead pump shall run continuously. A pressure reducing valve shall be installed on the discharge side of each constant speed pump.

- 18-29-606.5.1.2.1  Gravity tanks.

Gravity tanks operating at atmospheric pressure shall be installed as required by Section 18-29-606.5.4.

- 18-29-606.5.1.2.2  Total pressure.

The water piping system and equipment supplied by the systems enumerated in this section shall be capable of withstanding the total pressure developed by any such system at any elevation in which these pressures occur.

- 18-29-606.5.1.2.3  Low pressure cutoff.

When a pump is directly connected to a city water main, a low pressure cutoff switch on the pump shall be installed to prevent the creation of pressures less than 5 psi (35 kPa) on the suction side of the water system and within 5 feet (1525 mm) of the pump suction inlet, and a pressure gauge shall be installed between the shutoff valve and pump.

Exception: Fire pumps.

- 18-29-606.5.2  Surge tank for pumps.

When a water system in any building, structure or premises is supplied with other than city water or is equipped for service other than from the city mains or which is supplied with city water which has been previously used for any purpose, each service from the city water system shall enter through a receiving tank for the purpose of preventing water from the secondary system from flowing back into the city mains.

- 18-29-606.5.3  Check valves required.

Check valves which are noiseless in their operation and air chambers of sufficient air cushion capacity shall be installed in the suction pipe and the discharge pipe of each house pump, or other water pressure increasing device. Where such check valves are of the slow-acting type and the operation thereof entirely eliminates the shocks, strains, stresses, and excess noises caused by the operation of such pump or device, the installation of air chambers may be dispensed with.

- 18-29-606.5.3.1  Approval required.

No check valve shall be installed unless the design and construction thereof shall first have been approved by the commissioner of water.

- 18-29-606.5.4  Equipment required for tanks receiving city water.

All surge tanks, receiving reservoirs, gravity storage tanks, house storage tanks, or tanks of any description used for receiving or storing city water at atmospheric pressure, shall be supplied an approved slow-acting automatic control valve. The discharge outlet of the control valve shall be directly connected to the receiving unit at a distance of 6 inches (150 mm) above the top of a horizontal overflow pipe. For a vertical overflow pipe, the distance shall be 6 inches (150 mm) plus the diameter of the overflow pipe. The overflow pipe connection shall have an area of not less than twice that of the supply opening.

- 18-29-606.5.4.1  Sludge drain pipe.

Each tank used for receiving or storing city water shall be provided with a sludge drain pipe which shall be connected to the tank at the lowest level of the bottom section thereof and shall discharge through an indirect connection to the drainage system with a minimum air gap of 6 inches (150 mm).

- 18-29-606.5.4.2  Size.

Each sludge drain pipe shall be equal in size to the inlet pipe but need not exceed 2 inches (50 mm) and shall be provided with a control valve with a clear waterway equal in area to that of the sludge drain pipe.

- 18-29-606.5.4.3  Covers and support.

Such tanks shall have bolted watertight covers of the same material as the tank and shall be located and housed to prevent external pollution.  The building commissioner shall approve the support for all such tanks before the permit is issued.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-606.5.5  Recycling system for vehicle wash installations.

All new or newly remodeled commercial and industrial vehicle wash installations shall be equipped with a water recycling system to conserve water. The system shall be composed of a water reuse tank and all necessary piping to insure the cycling of water for more than one washing operation.

- 18-29-606.5.6  Potable water inlet control and location.

Potable water inlets to gravity tanks shall be controlled by a ball cock or other automatic supply valve to prevent the tank from overflowing. The inlet shall be terminated as to provide an air gap not less than 4 inches (100 mm) above the overflow.

- 18-29-606.5.7  Tank drain pipes.

A valved pipe shall be provided at the lowest point of each tank to permit emptying of the tank. The tank drain pipe shall discharge as required for overflow pipes.

- 18-29-606.5.8  Prohibited location of potable supply tanks.

Potable water gravity tanks or manholes of potable water pressure tanks shall not be located directly under any soil or waste piping or any source of contamination.

- 18-29-606.5.9  Pressure relief valve requirements.

Each pressure relief valve shall be a minimum of 3/4 inch (20 mm) and shall be equipped with a test lever. In addition, an automatic vacuum relief valve shall be installed on such tanks with a 24-mesh screen of bronze or stainless steel. The area of the screening shall be 50 percent greater than the opening it serves. All equipment of a hydropneumatic system shall be capable to withstand the designed working pressure.

Exception: This section shall not apply to pressurized captive air diaphragm/bladder tanks.

- 18-29-606.5.10  Pressure relief valves for hydropneumatic tanks.

Every pressure tank in a hydropneumatic pressure booster system shall be protected with a pressure relief valve. The pressure relief valve shall be set at a maximum pressure equal to the rating of the tank. The relief valve shall be installed on the supply pipe to the tank or on the tank. The relief valve shall discharge by gravity to a safe place of disposal.

- 18-29-606.6  Test of distribution pipes.

The entire water distribution system within buildings shall be tested in the presence of a plumbing inspector utilizing a water or air pressure test. All piping, fittings, valves and equipment except any atmospheric tank shall be tested to 1 1/2 times its designed pressure but not less than 100 psi (690 kPa). When the test pressure exceeds 100 psi (690 kPa) only a hydrostatic test shall be given.

- 18-29-607  Hot Water Supply System.

- 18-29-607.1  Where required.

In occupied structures, hot water shall be supplied to all plumbing fixtures and equipment utilized for bathing, washing, culinary purposes, cleansing, laundry or building maintenance. Every sink and lavatory shall be supplied with hot and cold water. No water exceeding 140°F (60°C) shall discharge into any lavatory, sink, tub or shower.

Exception: In nonresidential occupancies, hot water or tempered water shall be supplied for bathing and washing purposes. Tempered water shall be delivered from accessible hand-washing facilities.

- 18-29-607.1.1  Water temperature.

All lavatory faucets for public use shall be provided with an automatic safety water mixing device to prevent sudden unanticipated changes in water temperature or excessive water temperatures. The automatic safety water mixing device shall be either thermostatic, pressure balance or combination controlled, in accordance with ANSI/ASSE 1016 or 1017, ASSE-1066 adjusted to a maximum setting of 115°F (46°C) at the time of installation.

- 18-29-607.1.2  Shower compartments and shower- bath combinations.

All shower compartments and shower-bath combinations shall be provided with an automatic safety water mixing device to prevent sudden unanticipated changes in water temperature or excessive water temperatures. The automatic safety water mixing device shall be either thermostatic, pressure balance, or combination controlled, in accordance with ANSI/ASSE 1016 and designed with a maximum handle rotation limit/stop, adjusted to a maximum setting of 115°F (46.1°C).

- 18-29-607.1.2.1  Mixed water temperature.

The temperature of mixed water provided to multi- shower units or gang showers shall be controlled by a master automatic safety water mixing device or individually regulated by automatic safety mixing valves for each shower unit. A hot water heater thermostat shall not be an acceptable alternative water temperature control device.

- 18-29-607.2  Heated plumbing circulating system.

Hot water supply systems in buildings other than one-family and two-family dwellings shall be of the return circulation type in buildings where the developed length of hot water piping, from the source of hot water supply to the farthest fixture supplied, exceeds 100 feet (30.5 m).

- 18-29-607.2.1  Return piping.

The return piping shall be sized for a maximum temperature drop of 20°F (6.67°C) for forced circulation systems and 40°F (4.44°C) for gravity circulation systems. Such piping may be of the upfeed system, downfeed system or the combination upfeed and downfeed systems and shall be installed as follows:

1.     For upfeed systems, the return circulation pipe shall connect so the supply risers below the top-most supply branch to fixtures and not more than 12 inches (300 mm) below.

2.     For downfeed systems and combination upfeed and downfeed systems, the return circulation pipe shall connect to the base of each downfeed riser.

3.     For inverted downfeed systems, the return circulation pipe shall connect to the supply risers above the lowest supply branch to fixtures and not more than 12 inches (300 mm) above.

4.     For inverted upfeed systems and inverted combination downfeed and upfeed systems, the return circulation pipe shall connect to the top of the riser above the highest fixture.

5.     Return circulation pipes shall connect to the water heater or storage tank. Each return circulation riser branch shall be provided with a shutoff valve and check valve. Where more than one return circulation riser connects to a return main, each return circulation riser branch shall be provided with a shutoff valve, check valve and balancing valve or a check valve and combination shutoff balancing valve. All trapped piping shall be provided with an automatic air vent at the highest point.

- 18-29-607.2.1  Piping insulation.*

Piping in required return circulation systems shall be insulated to provide a thermal resistance, R, excluding film resistances, of

R= [t1-t0(hr)(Ft2)°F.]/Btu

25

For SI: R = [t1 - t0(0.0304)K x m2]/W

where t1 - t0 is the design temperature differential between the water in the pipe and the surrounding air in degrees Fahrenheit (°F).

Exception: Pipe insulation is not required where t1 - t0 is 25°F (14°C) or less.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; section numbering duplicates that of the immediately preceding section.

- 18-29-607.2.2  Pump operation.

Where a circulating pump is installed on a return circulation hot water system, the pump shall be arranged to shut off automatically or to allow manual shut off when the hot water system is not in operation.

- 18-29-607.3  Thermal expansion control.

A means of controlling increased pressure caused by thermal expansion shall be provided where required in accordance with Sections 18-29-607.3 and 18-29-607.3.2.

- 18-29-607.3.1  Pressure reducing valve.

For water service system sizes up to and including 2 inches (50 mm), a device for controlling pressure shall be installed where thermal expansion has caused the pressure on the downstream side of a pressure reducing valve to exceed the main supply pressure. A pressure reducing valve with an integral bypass check valve or other device shall be installed to satisfy this requirement.

- 18-29-607.3.2  Backflow prevention device or check valve.

Where a backflow prevention device, check valve or other device is installed on a water supply system utilizing storage water heating equipment such that thermal expansion causes an increase in pressure, a device for controlling pressure shall be installed.

- 18-29-607.4  Hot water supply to fixtures.

The hot water supply to any fixture requiring hot water shall be installed on left side of the fixture.

- 18-29-607.5  Expansion joints.

Mechanical expansion joints shall be accessible and may be used where necessary to provide for expansion and contraction of the pipes. For hot water piping, the expansion function shall be provided by the flexing of the piping material with expansion loops or swing joints. The piping shall be properly anchored and installed as follows:

1.     Each hot water riser shall be provided with anchors at a maximum distance of 100 feet (30.5 m) or less with an expansion loop of required length provided between such anchors.

2.     Each hot water main shall be provided with anchors at a maximum distance of 100 feet (30.5 m) or less with an expansion loop of required length provided between such anchors. Offsets of 90 degrees in a horizontal main shall be of required length to absorb expansion by flexure.

3.     Branches from mains connected to risers shall be provided with a swing joint of required length unless the branch is of adequate length to absorb expansion by flexure.

4.     Branches from risers to fixtures shall be provided with a swing joint of required length unless the branch is of adequate length to absorb expansion by flexture.

- 18-29-607.6  Prohibited connections.

Any water pipe connection to any pump or other appliance through which any vibration, shock, strain, stress, or pulsation may effectuate a water hammer is prohibited. Any excess noises or sounds in the water supply system of any building or structure that may be communicated through such connection or service pipe of the Chicago Waterworks System is also prohibited.

- 18-29-608  Protection of Potable Water Supply.

- 18-29-608.1  General.

A potable water supply system shall be designed, installed and maintained in such a manner so as to prevent contamination from nonpotable liquids, solids or gases being introduced into the potable water supply through cross-connections or any other piping connections to the system. Backflow preventer applications shall conform to Table 18-29-608.1.

Table 18-29-608.1
Application for Backflow Preventers

For a printer-friendly PDF version of Table 18-29-608.1, please click here.

Device; Degree of Hazard a; Application b; Applicable Standards. Air gap c; High or low hazard; Backsiphonage or backpressure; ASME A112.1.2. Antisiphon-type Water Closet Flush Tank Ball Cock; Low Hazard; Backsiphonage only; ASSE 1002 CSA CAN/CSA-B125. Reduced Pressure Principle Backflow Preventer; High or low hazard; Backpressure or backsiphonage Sizes 1/4" to 10"; ASSE 1013 AWWA C511 CSA CAN/CSA B64.4. Reduced Pressure Detector Assembly Backflow Preventer; High or low hazard; Backsiphonage or backpressure; ASSE 1047. Double Check Backflow Prevention Assembly; Low hazard; Backpressure or backsiphonage Sizes 3/8" to 16"; ASSE 1015 AWWA C510. Double Check Detector Backflow Preventer Assembly; Low hazard; Backpressure or backsiphonage (Fire sprinkler systems) Sizes 1 1/2" - 16"; ASSE 1048. Dual Check Valve-Type Backflow Preventer; Low hazard; Backpressure or backsiphonage Sizes 1/4" - 1"; ASSE 1024. Backflow Preventer with Intermediate Atmospheric Vents; Low hazard; Backpressure or backsiphonage Sizes 1/4" - 3/4"; ASSE 1012 CSA CAN/CSA-B64.3. Dual Check Valve-Type Backflow Preventer for Carbonated Beverage Dispensers/Post Mix Type; Low hazard; Backpressure or backsiphonage Sizes 1/4" - 3/8"; ASSE 1032. Pipe-Applied Atmospheric-Type Vacuum Breaker; High or low hazard; Backsiphonage only Sizes 1/4" - 4"; ASSE 1001 CSA CAN/CSA-B64.1.1. Pressure Vacuum Breaker Assembly; High or low hazard; Backsiphonage only Sizes 1/2" - 2"; ASSE 1020. Hose-connection Vacuum Breaker; High or low hazard; Backsiphonage Sizes 1/2", 3/4", 1"; ASSE 1011 CSA CAN/CSA-B64.2. Vacuum Breaker Wall Hydrants, Frost-Resistant, Automatic Draining Type; High or low hazard; Backsiphonage Sizes 3/4", 1"; ASSE 1019 CSA CAN/CSA-B64.2.2. Laboratory Faucet Backflow Preventer (Non-testable); Low hazard; Backsiphonage; ASSE 1035 CSA B64.7. Hose Connection Backflow Preventer (Non-testable); Low hazard; Low head backpressure, rated working pressure backpressure or backsiphonage Sizes 1/2" - 1"; ASSE 1052. Spill-proof vacuum breaker; High or low hazard; Backsiphonage only Sizes 1/4" - 2"; ASSE 1056.

For SI: 1 inch = 25.4 mm

a Low Hazard - See Pollution (Section 202) and Department of Water requirements

High Hazard - See Contamination (Section 202) and Department of Water requirements

b See Backpressure (Section 202)

See Backpressure, Low Head (Section 202)

See Backsiphonage (Section 202)

c Break tank

d For systems using non-food grade chemical additives

- 18-29-608.2  Plumbing fixtures.

The supply lines or fittings for every plumbing fixture shall be installed so as to prevent backflow.

- 18-29-608.3  Water supply pipes.

Water supply pipe to plumbing fixtures, water using appliances and equipment, wall hydrants (except fire hydrants used for fire fighting) and hose bibbs shall meet the following requirements:

1.     No plumbing fixture shall be installed unless the water supply enters said fixture with an air gap of twice the internal diameter of the water supply pipe but not less than 1 inch (25 mm) above the flood level rim of the fixture, except for fixtures listed in Section 11-8-500* of this article.

* Editor's note – Coun. J. 3-28-01, p. 55444, § 1, repealed former chapter 11-8 and inserted new chapter 18-29; correct internal reference appears to be to either Section 18-29-401 or Section 18-29-423.

2.     Dishwashing machine and clothes washing machine water supply pipes shall have an air gap as required for plumbing fixtures, except that dishwashing machine water supply pipes may enter through an approved atmospheric vacuum breaker located on the discharge side of the last control valve. The bottom of the vacuum breaker shall not be less than 6 inches (150 mm) above the flood level rim of the machine or related equipment.

- 18-29-608.3.1  Special equipment, water supply protection.

The water supply for hospital fixtures shall be protected against backflow with a reduced pressure principle backflow preventer, an atmospheric vacuum breaker, or an air gap. Vacuum breakers for bedpan washer hoses shall not be located less than 5 feet (1525 mm) above the floor.

- 18-29-608.4  Deliberately omitted.

- 18-29-608.5  Secondary water.

See Article 2 for definition. For materials for secondary water refer to Table 18-29-605.5, Water Distribution Pipe.

- 18-29-608.6  Prohibited use of secondary water.

No secondary water shall overflow or be discharged into any surge tank, storage tank, or reservoir, or shall in any way be piped or conveyed into the water supply system or into any building, structure, or premises, such that the overflow or discharge contaminates the fresh water supply from the mains of the Chicago Waterworks System either inside of the premises or in the water service pipe. Secondary water shall not be piped to or used in any plumbing fixture, or for cooling crushers, rollers, or mixers where foods, candies, liquids or materials are manufactured for human or animal consumption.

In accordance with Section 11-8-390 of this Code, the installation of any potable water supply well after May 14, 1997 is prohibited except as otherwise permitted in that section.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-608.6.1  Private water supplies.

Cross-connections between a private water supply and a potable public supply shall be prohibited.

- 18-29-608.7  Stop-and-waste valves prohibited.

Combination stop-and-waste valves or cocks shall not be installed underground.

- 18-29-608.8  Identification of potable and nonpotable water.

In all buildings where two or more water distribution systems (one potable water and the other nonpotable water) or secondary water distribution systems are installed, each system shall be identified either by color marking or metal tags as required by ASME A13.1.

- 18-29-608.9  Re-utilization prohibited.

Water utilized for the cooling of equipment of other processes shall not be returned to the potable water system. Such water shall be discharged into a drainage system through an air gap or shall be utilized for nonpotable purposes.

- 18-29-608.10  Reuse of piping.

Piping that has been utilized for any purpose other than conveying potable water shall not be utilized for conveying potable water.

- 18-29-608.11  Painting of water tanks.

The interior surface of a potable water tank shall not be lined, painted or repaired with any material that changes the taste, odor, color or potability of the water supply when the tank is placed in, or returned to, service.

- 18-29-608.12  Pumps and other appliances.

Water pumps, filters, softeners, tanks and all other devices that handle or treat potable water shall be protected against contamination.

- 18-29-608.13  Backflow protection.

Means of protection against backflow shall be provided in accordance with Sections 18-29-608.13.1 through 18-29-608.13.6.

- 18-29-608.13.1  Air gap.

The minimum required air gap shall be measured vertically from the lowest end of a potable water outlet to the flood level rim of the fixture or receptacle into which such potable water outlet discharges.

- 18-29-608.13.2  Reduced pressure principle backflow preventers.

Reduced pressure principle backflow preventers shall conform to ASSE 1013, AWWA C511 or CSA CAN/CSA-B64.4. These devices shall be permitted to be installed in areas subject to continuous pressure conditions. The relief opening shall discharge by air gap and shall be prevented from being submerged.

- 18-29-608.13.3  Backflow preventer with intermediate atmospheric vent.

Backflow preventers with intermediate atmospheric vents shall conform to ASSE 1012 or CSA CAN/CSA- B64.3. These devices shall be permitted to be installed in areas subject to continuous pressure conditions. The relief opening shall discharge by air gap and shall be prevented from being submerged.

- 18-29-608.13.4  Barometric loop.

Barometric loops shall precede the point of connection and shall extend vertically to a height of 35 feet (10.67 m). A barometric loop shall only be utilized as an atmospheric-type or pressure-type vacuum breaker.

- 18-29-608.13.5  Atmospheric-type vacuum breakers.

Pipe-applied atmospheric-type vacuum breakers shall conform to ASSE 1001 or CSA CAN/CSA- B64.1.1. Hose-connection vacuum breakers shall conform to ASSE 1011, CSA CAN/CSA-B64.2, ASSE 1019, CSA CAN/CSA-B64.2.2, ASSE 1035, CSA B64.7 or ASSE 1052. These devices shall operate wider normal atmospheric pressure when the critical level is installed at the required height.

- 18-29-608.13.6  Double check-valve assemblies.

Double check-valve assemblies shall conform to ASSE 1015 or AWWA C510. Double-detector check-valve assemblies shall conform to ASSE 1048. These devices shall be capable of operating under continuous pressure conditions.

- 18-29-608.14  Location of backflow preventers.

Access shall be provided to backflow preventers as specified by the installation instructions of the approved manufacturer.

- 18-29-608.15  Protection of potable water outlets.

All potable water openings and outlets shall be protected against backflow in accordance with the following:

1.     Openings and outlets shall be protected by an air gap between the opening and the fixture flood level rim as specified in Table 18-29-608.15.1. Openings and outlets equipped for hose connection shall be protected by means other than an air gap.

2.     Openings and outlets shall be protected by a reduced pressure principle backflow preventer.

3.     Openings and outlets shall be protected by a backflow preventer with an intermediate atmospheric vent.

4.     Openings and outlets shall be protected by atmospheric-type vacuum breakers. The critical level of the vacuum breaker shall be set a minimum of 6 inches (150 mm) above the flood level rim of the fixture or device. Ball cocks shall be set in accordance with Section 425.3.1. Vacuum breakers shall not be installed under exhaust hoods or similar locations that will contain toxic fumes or vapors. Pipe-applied vacuum breakers shall be installed not less than 6 inches (150 mm) above the flood level rim of the fixture, receptor or device served.

5.     All pull-out spout-type faucets shall be in compliance with CSA CAN/CSA-B 125 and have an integral vacuum breaker or vent to atmosphere in their design or shall require a dedicated deck- or wall-mounted vacuum breaker. Approved deck-mounted or equipment-mounted vacuum breakers and faucets with integral atmospheric or spill-proof vacuum breakers shall be installed in accordance with the manufacturer's instructions and the requirements for labeling with the critical level not less than, 1 inch (25 mm) above the flood level rim.

6.     Sillcocks, hose bibbs, wall hydrants and other openings with a hose connection shall be protected by an atomospheric-type or pressure type vacuum breaker or a permanently attached hose connection vacuum breaker.

Exceptions:

1.     This section shall not apply to water heater and boiler drain valves that are provided with hose connection threads and that are intended for only tank or vessel draining.

2.     This section shall not apply to water supply valves intended for connection of clothes washing machines where backflow prevention is otherwise provided or is integral with the machine.

Table 18-29-608.15.1
Minimum Required Air Gaps

Fixture; Minimum Air Gap. Away from a wall a (inches); Close to a wall (inches). Lavatories and other fixtures with effective opening not greater than 1/2 inch in diameter; 1; 1 1/2. Sink, laundry trays, gooseneck back faucets and other fixtures with effective openings not greater than 3/4 inch in diameter; 1 1/2; 2 1/2. Over-rim bath fillers and other fixtures with effective openings not greater than 1 inch in diameter; 2; 3. Drinking water fountains, single orifice not greater than 7/16 inch in diameter or multiple orifices with a total area of 0.150 square inch (area of circle 7/16 inch in diameter).; 1; 1 1/2. Effective openings greater than 1 inch.; Two times the diameter of the effective opening.; Three times the diameter of the effective opening..

For SI: 1 inch = 25.4 mm.

a Applicable where walls or obstructions are spaced from the nearest inside edge of the spout opening a distance greater than three times the diameter of the effective opening for a single wall, or a distance greater than four times the diameter of the effective opening for two intersecting walls.

- 18-29-608.16  Connections to the potable water system.

Connections to the potable water system shall conform to Sections 18-29-608.16.1 through 18-29-608.16.6.

- 18-29-608.16.1  Beverage carbonator.

Every water supply pipe servicing a beverage carbonator shall receive its supply through a receiving tank constructed in accordance with Section 18-29-606.5.4 of this Article or shall have installed in the pipe an approved stainless steel in-line-pressure-type backflow preventer consisting of two check valves separated by an open air port conforming to ASSE 1012 or ASSE 1022. The air port shall not be directly connected to the drainage system.

- 18-29-608.16.1.1  Backflow preventer.

The backflow preventer shall be installed in an accessible location on the discharge side of the carbonator water supply valve. No copper tube or pipe or copper lined components shall be used for the receiving tank or its piping to the carbonator or the outlet of the stainless backflow preventer.

- 18-29-608.16.2  High-pressure steam boilers.

Steam boilers exceeding a pressure of 15 psi (103.4 kPa) and hydronic heating systems designed to exceed a pressure of 15 psi (103.4 kPa) or a temperature of 250°F (121°C) shall not be directly connected to the water supply system. Steam boilers not exceeding a pressure of 15 psi (103.4 kPa) and hydronic heating systems designed not to exceed pressure of 30 psi (306.9 kPa) or a temperature of 250°F (121°C) shall be provided with an in-line pressure-type backflow preventer consisting of two check valves separated by an open air port. The air port shall not be directly connected to the drainage system. The backflow preventer shall be installed in an accessible location on the discharge side of the boiler water supply valve and on the inlet side of the boiler feed valve.

- 18-29-608.16.3  Connections to automatic fire sprinkler systems and standpipe systems.

The potable water supply to automatic fire sprinkler and standpipe systems shall be protected against backflow by a testable double detector check-valve assembly.

- 18-29-608.16.4  Fire protection equipment, risers, standpipes, tanks to be drained and flushed.

All fire protection equipment, tanks, risers, standpipes, domestic house tanks, compression tanks and all other tanks that have a weight check valve for backflow prevention and are supplied with water from the Chicago Waterworks System shall be drained and flushed at least every 12 months in the presence of a plumbing inspector. Further, fire protection systems and equipment shall be kept free from accumulations of sand, silt, and stagnant water which would nullify the action of the chlorine content of city water.

- 18-29-608.16.5  Fire-extinguishing equipment cross-connection.

Any building, premises, material or storage yard which receives service from the Chicago Waterworks System shall not have a siamese or other connection for fire extinguishing purposes installed near any river, lake, or waterway where a city fire boat or city fire engine or pump may pump river, lake or shore water into the city water pipes through a cross-connection of any kind.

- 18-29-608.16.5.1  Prohibitions.

No stationary pump or privately owned fire equipment shall be maintained for emergency use which draws water from rivers, lakes, and waterways nor shall they use cisterns or wells adjacent to the rivers, lakes and waterways unless protected from cross-connections to city water systems.

- 18-29-608.16.6  Chemical or petroleum pressure vessels.

Chemical, contaminated water, or sewage lines or vessels shall comply with Sections 18-29-608.16.6.1 through Section 18-29-608.16.6.3.

- 18-29-608.16.6.1  Chemical or petroleum pressure vessels.

No person, corporation or firm shall connect any pressure vessel to the city water supply. This includes a storage tank, tank car, tank truck or trailer or other miscellaneous pressurized tank or cylinder containing or having contained liquefied gaseous petroleum products or other liquefied gaseous chemicals.

- 18-29-608.16.6.2  Water flushing or cooling.

Water for flushing or cooling (or to be otherwise instilled into such a vessel) shall be obtained by gravity through an indirect connection. If water under pressure is required, it may be supplied only by means of an auxiliary pump taking suction from a suction tank provided for this purpose only, with an over-rim supply having an indirect connection.

- 18-29-608.16.6.3  Chemical, contaminated water, or sewage lines or vessels.

There shall be no direct connection between the city water lines and lines, equipment or vessels containing raw or contaminated water, contaminating chemicals or sewage. Such connections shall be made only through and* indirect connection.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “an”.

- 18-29-608.16.7  Deliberately omitted.

- 18-29-608.16.8  Portable cleaning equipment.

Where the portable cleaning equipment (including power washers) connects to the water distribution system, the water supply system shall be protected against backflow in accordance with Section 18-29-608.13.1, Section 18-29-608.13.2, Section 18-29-608.13.3, Section 18-29-608.14 or Section 18-29-608.15.

- 18-29-608.16.9  Dental pump equipment.

Where dental pumping equipment connects to the water distribution system, the water supply system shall be protected against backflow in accordance with Section 18-29-608.13.1, Section 18-29-608.13.5, Section 18-29-608.13.6 or Section 18-29-608.15.

- 18-29-608.17  Private water supplies.

Private water supplies shall be in accordance with Sections 18-29-608.17.1 through 18-29-608.17.1.2.

- 18-29-608.17.1  Well locations.

A potable ground water source or pump suction line shall not be located closer to potential sources of contamination than the distances shown in Table 18-29-608.17.1. In the event the underlying rock structure is limestone or fragmented shale, the local or state health department shall be consulted on well site location.

Table 18-29-608.17.1
Distance from Sources of Contamination to Private Water Supplies and Pump Suction Lines

Source of Contamination; Distance (feet). Barnyard; 100. Farm silo; 25. Pasture; 100. Pumphouse floor drain of cast iron draining to ground surface; 2. Seepage pits; 50. Septic tank; 25. Sewer; 10. Subsurface disposal fields; 50. Subsurface pits; 50.

For SI: 1 foot = 304.8 mm.

- 18-29-608.17.1.1 Distances.

The distances outlined in Table 18-29-608.17.1 constitute minimum separation and shall be increased in areas of creviced rock or limestone, or when the direction of movement of ground water through sources of contamination is toward the well.

- 18-29-608.17.1.2  Direct connections.

No pipe or system of piping in any building, structure, or premises, which receives its supply from the Chicago Waterworks System shall be directly connected to any device, appliance, or apparatus in which such water supply is used to provide power through a water jet or other device to create vacuum or partial vacuum with which to operate any aspirator, syphon, cellar drainer, ejector, cleaner, sweeper, conveyor, or washer of any kind or description.

- 18-29-609  Health Care Plumbing.

- 18-29-609.1  General.

This section shall govern those aspects of health care plumbing systems that differ from plumbing systems in other structures. Health care plumbing systems shall conform to the requirements of this section in addition to the other requirements of this Article.

- 18-29-609.1.1  Where required.

The provisions of this section shall apply to the special devices and equipment installed and maintained in the following occupancies: nursing homes, homes for the aged, orphanages, infirmaries, first aid stations, psychiatric facilities, clinics, professional offices of dentists and doctors, mortuaries, educational facilities, surgery, dentistry, research and testing laboratories, establishments manufacturing pharmaceutical drugs and medicines, and other structures with similar apparatus and equipment classified as plumbing.

- 18-29-609.2  Water service.

All hospitals shall have two water service pipes installed in such a manner so as to minimize the potential for an interruption of the supply of water in the event of a water main or water service pipe failure.

- 18-29-609.3  Hot water.

Hot water shall be provided to supply all of the hospital fixture, kitchen and laundry requirements. Special fixtures and equipment shall have hot water supplied at a temperature specified by the manufacturer. The hot water system shall be installed in accordance with Sections 18-29-607 through 18-29-607.6.

- 18-29-609.4  Vacuum breaker installation.

Vacuum breakers shall be installed a minimum of 6 inches (150 mm) above the flood level rim of the fixture or device in accordance with Sections 18-29-608 through 18-29-608.17.1.2. The flood level rim of hose connections shall be the maximum height at which any hose is utilized.

- 18-29-609.5  Prohibited water closed* and clinical sink supply.

Jet- or water-supplied orifices, except those supplied by the flush connections, shall not be located in or connected with a water closet bowl or clinical sink. This section shall not prohibit an approved bidet installation.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “closet”.

- 18-29-609.6  Clinical, hydrotherapeutic and radiological equipment.

All clinical, hydrotherapeutic, radiological or any equipment that is supplied with water or that discharges to the waste system shall conform to the requirements of this section and Sections 18-29-608 through 18-29-608.17.1.2.

- 18-29-609.7  Condensate drain trap seal.

A water supply shall be provided for cleaning, flushing and resealing the condensate trap, and the trap shall discharge through an air gap in accordance with Sections 18-29-608 through 18-29-608.17.12.

- 18-29-609.8  Valve leakage diverter.

Each water sterilizer filled with water through directly connected piping shall be equipped with an approved leakage diverter or bleed line on the water supply control valve to indicate and conduct any leakage of unsterile water away from the sterile zone.

- 18-29-610  Disinfection of Potable Water System.

- 18-29-610.1  Scope.

Potable water systems or any part thereof installed or repaired shall be disinfected in accordance with one of the following methods before it is placed in operation:

1.     The system, or part thereof, shall be filled with a solution containing 50 parts per million of available chlorine and allowed to stand six hours before flushing and returning to service;

2.     The system, or part thereof, shall be filled with a solution containing 100 parts per million of available chlorine and allowed to stand two hours before flushing and returning to service;

3.     In the case of a potable-water storage tank where it is not possible to disinfect as provided in subsections 1 and 2, the entire interior of the tank shall be swabbed with a solution containing 200 parts per million of available chlorine and the solution allowed to stand two hours before flushing and returning to service.

- 18-29-611  Water Treatment Units.

- 18-29-611.1  Design.

Drinking water treatment units and filters shall meet the requirements of NSF 42 and NSF 53.

- 18-29-611.2  Reverse osmosis systems.

Reverse osmosis drinking water treatment systems shall meet the requirements of NSF 58. Waste or discharge from reverse osmosis or other types of water treatment units shall enter the drainage system through an air gap.

- Article 7.  Sanitary Drainage

- 18-29-701  General.

- 18-29-701.1  Scope.

The provisions of this article shall govern the materials, design, construction and installation of sanitary drainage systems.

- 18-29-701.2  Sewer required.

Every building in which plumbing fixtures are installed and every premises having drainage piping shall be connected to a public sewer, where available. When a public sewer is not available, drain pipes from buildings shall be connected to an approved system of sewage disposal.

- 18-29-701.3  Separate sewer connection.

Every building having plumbing fixtures installed and intended for human habitation, occupancy or use on premises abutting on a street, alley or easement in which there is a public sewer shall have a separate connection with the sewer in the street. New connections to the public sewer in alleys are not allowed.

- 18-29-701.4  Sewage treatment.

Sewage or other waste from a plumbing system that is deleterious to surface or subsurface waters shall not be discharged into the ground or into any waterway unless it has first been rendered innocuous through subjection to an approved form of treatment.

- 18-29-701.5  Damage to drainage system or public sewer.

Wastes detrimental to the public sewer system or detrimental to the functioning of the sewage-treatment plant shall be treated and disposed of as determined by the commissioner of sewers.

- 18-29-701.6  Tests.

The sanitary drainage system shall be inspected and tested in accordance with Sections 18-29-312 through 18-29-312.9.

- 18-29-701.7  Connections.

Direct connection of a steam exhaust, blowoff or drip pipe shall not be made with the building drainage system. Waste water when discharged into the building drainage system shall be at a temperature not higher than 180°F (78°C). When higher temperatures exist, approved cooling methods shall be provided.

- 18-29-702  Materials.

- 18-29-702.1  Above-ground sanitary drainage and vent pipe.

Above-ground soil, waste and vent pipe shall conform to the respective standard listed in Table 18-29-702.1. The use of polyvinyl chloride (PVC) plastic pipe shall be limited to buildings three stories or less in height intended for family occupancy. The use of DWV copper tubing shall not be permitted in any structure or plumbing system.

(Amend. Coun. J. 3-27-02, p. 82090, § 3)

Table 18-29-702.1
Above-Ground Drainage and Vent Pipe

Material; Standard. Brass pipe; ASTM B 43. Cast-iron pipe hub & spigot c; ASTM A 74; CISPI 301; ASTM A 888. Cast iron pipe hubless a; ASTM A 888; CISPI 301. Copper or copper-alloy pipe; ASTM B 42; ASTM B 302. Copper or copper-alloy tubing (Type K, L, or M); ASTM 75; ASTM B 88; ASTM B 251; ASTM B 306. Galvanized steel pipe; ASTM A 53. Glass pipe b; ASTMC 1053. Ductile iron pipe b; AWWA C151; AWWA C115. Polyvinyl chloride (PVC) a plastic pipe (Schedule 40); ASTM D 2665; ASTM D 2449; ASTM F 891 d; CSA CAN/CSA-B181.2. High silicon content cast iron pipe b; ASTM A 377-1984. Polypropylene or Polyvinylfluorodene (PVDF) a, b; ASTM F1412.

a In any building three stories or less in height for family occupancy only.

b Approved for acid waste only, on private system, not to be connected to the public sewer.

c Lead and oakum joints only.

d Use shall be limited to gravity drainage and venting only and shall not be allowed for pressurized drain, waste or venting applications.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-702.2  Underground building drainage and vent pipe.

Underground building sanitary drainage and vent pipe shall conform to the respective standard listed in Table 18-29-702.2 except that polyvinyl chloride (PVC) shall not be allowed.

Table 18-29-702.2
Underground Building Drainage and Vent Pipe

Material; Standard. Cast-iron pipe hub & spigot b; ASTM A 74; CISPI 301; ASTM A 888. Glass pipe a; ASTM C 1053. Copper or copper-alloy tubing (Type K); ASTM B 75; ASTM B 88; ASTM B 251. Polypropylene or Polyvinylfluorodene (PVDF) a; ASTM F1412. Ductile iron pipe; AWWA C151; AWWA C115. High silicon content cast iron pipe a; ASTMA A 377-1984.

a For acid waste only, on private system, not to be connected to the public sewer.

b The use of cast iron pipe shall be limited to construction within private property. Cast iron pipe will not be allowed in the public way.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-702.3  Building sewer pipe.

Building sewer pipe shall conform to the respective standard listed in Table 18-29-702.3 except that polyvinyl chloride (PVC) shall not be allowed for underground building and vent pipe except for subsurface soil drainage. The use of cast-iron pipe will be allowed in the public way.

(Amend. Coun. J. 3-27-02, p. 82090, § 3)

Table 18-29-702.3
Building Sewer Pipe

Material; Standard. Cast-iron pipe hub & spigot b; ASTM A 74; ASTM A 888; CISPI 301. Ductile iron pipe; AWWA C151; AWWA C115. Concrete pipe 24" or larger; ASTM C 14; ASTM C 76; CSA A257.1; CSA CAN/CSA A 257.2. Copper or copper-alloy tubing (Type K); ASTM D 1785; ASTM B 88; ASTM B 251. Polyvinyl chloride (PVC) plastic pipe (Schedule 40); ASTM D 1785; ASTM D 2665; ASTM D 2672; CSA CAN/CSA-B 137.3. Glass pipe a. Polypropylene or Polyvinylfluorodene (PVDF) a; ASTM F1412; ASTM D 4101. High silicon content cast- iron pipe b; ASTM F 492-1985. Extra strength vitrified clay pipe, 21" or smaller; ASTM C 4; ASTM C 700.

a For acid waste underground only, on private system, not to be connected to the public sewer.

b The use of cast-iron pipe shall be limited to construction within private property. Cast-iron pipe will not be allowed in the public way.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-702.4  Fittings.

Pipe fittings shall be approved for installation with the piping material installed and shall conform to the respective pipe standard listed in Table 18-29-702.4.

Table 18-29-702.4
Pipe Fittings

Material; Standard. Cast-iron pipe hub & spigot; ASME B 16; ASME B16.12; ASTMA 74; ASTM A 888; CISPI 301. Cast iron hubless c; ASTM A 888; CISPI 301. Copper or copper alloy; ASME B16.15; ASME B16.18; ASME B16.22; ASME B16.2-3; ASME B16.26; ASME B16.29; ASME B16.32. Glass b; ASTM C 1053. Polypropylene or Polyvinylfluorodene (PVDF) b; ASTM F11412; ASTM D4101. Gray iron and ductile iron a; AWWA C110. Malleable iron; ASME B16.3. Polyvinyl chloride (PVC) plastic c; ASTM D 3311. Steel; ASME B16.9; ASME B16.11; ASME B16.28. High Silicon content cast iron pipe b; ASTM F492-1985. Ductile iron pipe; AWWA C151; AWWA C115.

a May be used on aboveground storm and sanitary only.

b For acid waste piping only.

c In any building three stories or less in height for family occupancy only.

- 18-29-702.5  Chemical waste system.

A chemical waste system shall be completely separated from the sanitary drainage system. The chemical waste shall be treated in accordance with Section 18-29-803.2 before discharging to the sanitary drainage system. Separate drainage systems for chemical wastes and vent pipes shall be of an approved material that is resistant to corrosion and degradation for the concentrations of chemicals involved.

- 18-29-702.5.1  Glass pipe.

All glass pipe shall be of corrosion resistant pre- stressed low expansion borosilicate glass. Couplings shall be made with gasketing of equal corrosion resistant characteristics.

Table 18-29-702.5.1
Wall Thickness of Glass Pipe and Fittings

Standard Schedule; Heavy Schedule. Inches; Millimeters; Inches; Millimeters. 1 1/2 - 0.12; 38 mm - 3 mm; 1 1/2 - 0.17; 38 mm - 4 mm. 2 - 0.14; 50 mm - 4 mm; 2 - 0.17; 50 mm - 4 mm. 3 - 0.17; 75 mm - 4 mm; 3 - 0.20; 75 mm - 5 mm. 4 - 0.20; 100 mm - 5 mm; 4 - 0.26; 100 mm - 7 mm. 6 - 0.24; 150 mm - 6 mm; 6 - 0.33; 150 mm - 8 mm.

- 18-29-702.5.1.1  Padding.

Padded hangers for horizontal runs shall be used and be properly supported. All riser clamps for vertical line shall be padded with resilient rubber or equally resilient material.

- 18-29-702.5.1.2  Thickness.

Wall thickness of the glass pipe and fitting shall follow the specifications in Table 18-29-702.5.1.

- 18-29-702.5.1.3  Buried pipe.

The pipe to be buried shall be of heavy schedule. Below grade compression couplings shall have an outer shell of A1SI 300 series stainless steel or material of equal corrosion resistance. All piping and fittings shall be free of scratches. Underground piping, fittings and compression couplings shall be protected from direct contact with the earth or backfill material.

- 18-29-702.6  Safe pan material and construction.

All safe pan material and construction shall meet the requirements set forth in Sections 18-29-702.6.1 through 18-29-702.6.2.

- 18-29-702.6.1  Material.

Safe pans shall be made only of lead, copper, PVC or fiberglass, and shall meet the following requirements:

1.     Lead sheets for safe pans shall weigh at least four pounds per square foot;

2.     Copper sheets for safe pans shall weigh at least 12 ounces per square foot;

3.     PVC safe pans or liners shall be 30 ml or 40 ml.

- 18-29-702.6.2  Construction.

All safe pans shall be constructed with preformed dam corners, shall be watertight, adequately reinforced and provided with a drain opening designed to make a watertight joint. PVC safe pans and liners shall be solvent welded together with the proper cement.

- 18-29-703  Building Sewer.

- 18-29-703.1  Building sewer pipe near the water service.

Where the building sewer is installed within 10 feet (3.05 m) of the water service, as provided for in Section 18-29-603.2 the building sewer pipe shall conform to the respective standard for cast-iron pipe, copper or copper-alloy tubing listed in Table 18-29-702.3.

- 18-29-703.2  Drainage pipe in filled ground.

Where a building sewer or building drain is installed on filled or unstable ground, the drainage pipe shall conform to the respective standard for cast-iron pipe, copper or copper-alloy tubing as listed in Table 18-29-702.3.

- 18-29-703.3  Sanitary and storm sewers.

Where separate systems of sanitary drainage and storm drainage are installed in the same property, the sanitary and storm building sewers or drains shall be permitted to be laid side by side in one trench.

(Amend Coun. J. 5-7-03, p. 621, § 1)

- 18-29-703.3.1  Combined sewers.

For combined sewers refer to Sections 18-29-1104 and 18-29-1108.

(Amend Coun. J. 5-7-03, p. 621, § 1)

- 18-29-703.4  Existing building sewers and drains.

Existing building sewers and drains shall connect with new building sewer and drainage systems only when found by examination and test to conform to the new system in quality of material. The building commissioner shall notify the owner to make the changes necessary to conform to this chapter.

- 18-29-703.4.1  Inspection of existing underground building sewers for drain and reuse.

Existing underground building sewers, regardless of their age, may be reused if the pipe has been inspected by closed circuit television in the presence of personnel of the department of sewers as directed by the commissioner of sewers.

- 18-29-704  Drainage Piping and Installation.

- 18-29-704.1  Slope of horizontal drainage piping.

Horizontal drainage piping shall be installed in uniform alignment at uniform slopes. The minimum slope of a horizontal drainage pipe shall be in accordance with Table 18-29-704.1.

Table 18-29-704.1
Slope of Horizontal Drainage Pipe

Size (inches); Minimum Slope (inch per foot). 2 1/2 or less; 1/4. 3 to 6; 1/8. 8 or larger; 1/16.

- 18-29-704.2  Change in size.

The size of the drainage piping shall not be reduced in size in the direction of the flow. A 4-inch by 3-inch (100 mm by 75 mm) water closet connection shall not be considered as a reduction in size.

- 18-29-704.3  Connections to offsets and bases of stacks.

Horizontal branches shall connect to the bases of stacks at a point located not less than 10 pipe diameters downstream from the stack. Except as prohibited by Section 18-29-711.2, horizontal branches shall connect to horizontal stack offsets at a point located not less than 10 pipe diameters downstream from the upper stack.

- 18-29-704.4  Future fixtures.

Drainage piping for future fixtures shall terminate with an approved cap or plug.

- 18-29-704.5  Dead ends.

In the installation or removal of any part of a drainage system, dead ends shall be prohibited. Cleanout extensions and approved future fixture drainage piping shall not be considered as dead ends.

- 18-29-704.5.1  Freezing.

No soil or waste pipe shall be installed or permitted outside of a building or in an exterior wall unless provisions are made to protect such piping from freezing. This does not prohibit a soil or waste pipe from extending from a manufactured or mobile home unit to an approved point of discharge, provided such waste line is protected from freezing.

- 18-29-704.5.2  Deliberately omitted.

- 18-29-705  Joints.

- 18-29-705.1  General.

This section contains provisions applicable to joints specific to sanitary drainage piping.

- 18-29-705.2  Deliberately omitted.

- 18-29-705.3  Deliberately omitted.

- 18-29-705.4  Brass.

Joints between brass pipe or fittings shall comply with Sections 18-29-705.4.1 through 18-29-705.4.4.

- 18-29-705.4.1  Brazed joints.

All joint surfaces shall be cleaned. An approved flux shall be applied where required. The joint shall be brazed with a filler metal conforming to AWS A5.8.

- 18-29-705.4.2  Mechanical joints.

Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-705.4.3  Threaded joints.

Threads shall conform to ASME B 120.1. Pipe joint compound or tape shall be applied on the male threads only.

- 18-29-705.4.4  Welded joints.

All joint surfaces shall be cleaned. The joint shall be welded with an approved filler metal.

- 18-29-705.5  Cast iron.

Joints between cast-iron pipe or fittings shall comply with Sections 18-29-705.5.1 through 18-29-705.5.3.

- 18-29-705.5.1  Caulked joints.

Joints for hub and spigot pipe shall be firmly packed with oakum or hemp. Molten lead shall be poured in one operation to a depth of not less than 1 inch (25 mm). The lead shall not recede more than 1/8 inch (3 mm) below the rim of the hub and shall be caulked tight. Paint, varnish or other coatings shall not be permitted on the jointing material until after the joint has been tested and approved. Lead shall be run in one pouring and shall be caulked tight. Acid-resistant rope and acid-proof cement shall be permitted.

- 18-29-705.5.2  Compression gasket joints.

Compression gaskets shall conform to ASTM C 564. Gaskets shall be compressed when the pipe is fully inserted.

- 18-29-705.5.3  Mechanical joint coupling.

Mechanical joint couplings shall comply with CISPI 310 or ASTM C 1277 and shall meet the requirements of Factory Mutual Standard 1680, Class I, with a minimum working pressure of 15 psi (103.4 kPa). The elastomeric sealing sleeve shall conform to ASTMC 564 or CSA CAN/CSA-B602 and shall be provided with a center stop. Mechanical joint couplings shall be installed in accordance with the manufacturer's installation instructions.

- 18-29-705.6  Concrete joints.

Joints between concrete pipe or fittings shall be made with an elastomeric seal conforming to ASTM C 443, ASTM C 1173, CSA-A257.3 or CSA CAN/CSA- B602.

- 18-29-705.7  Copper pipe.

Joints between copper or copper-alloy pipe or fittings shall comply with Sections 18-29-705.7.1 through 18-29-705.7.5.

- 18-29-705.7.1  Brazed joints.

All joint surfaces shall be cleaned. An approved flux shall be applied where required. The joint shall be brazed with a filler metal conforming to AWS A5.8.

- 18-29-705.7.2  Mechanical joints.

Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-705.7.3  Soldered joints.

Solder joints shall be made in accordance with the methods of ASTM B 828. All cut tube ends shall be reamed to the full inside diameter of the tube end. All joint surfaces shall be cleaned. A flux conforming to ASTM B 813 shall be applied. The joint shall be soldered with a solder conforming to ASTM B 32.

- 18-29-705.7.4  Threaded joints.

Threads shall conform to ASME B 120.1. Pipe joint compound or tape shall be applied on the male threads only.

- 18-29-705.7.5  Welded joints.

All joint surfaces shall be cleaned. The joint shall be welded with an approved filler metal.

- 18-29-705.8  Copper tubing.

Joints between copper or copper-alloy tubing or fittings shall comply with Sections 18-29-705.8.1 through 18-29-705.8.3.

- 18-29-705.8.1  Brazed joints.

All joint surfaces shall be cleaned. An approved flux shall be applied where required. The joint shall be brazed with a filler metal conforming to AWS A5.8.

- 18-29-705.8.2  Mechanical joints.

Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-705.8.3  Soldered joints.

Solder joints shall be made in accordance with the methods of ASTM B 828. All cut tube ends shall be reamed to the full inside diameter of the tube end. All joint surfaces shall be cleaned. A flux conforming to ASTM B 813 shall be applied. The joint shall be soldered with a solder conforming to ASTM B 32.

- 18-29-705.9  Borosilicate glass joints.

Glass-to-glass connections shall be made with a belted compression-type stainless steel (300 series) coupling with contoured acid-resistant elastomer compression ring and a fluorocarbon polymer inner seal ring or with caulked joints in accordance with Section 18-29-705.9.1.

- 18-29-705.9.1  Caulked joints.

Every lead-caulked joint for hub and spigot soil pipe shall be firmly packed with oakum or hemp and filled with molten lead not less than 1 inch (25 mm) deep and not to extend more than 1/8 inch (3 mm) below the rim of the hub. Paint, varnish or other coatings shall not be permitted on the jointing material until after the joint has been tested and approved. Lead shall be run in one pouring and shall be caulked tight. Acid-resistant rope and acid-proof cement shall be permitted.

- 18-29-705.10  Steel.

Joints between galvanized steel pipe or fittings shall comply with Sections 18-29-705.10.1 and 18-29-705.10.2.

- 18-29-705.10.1  Threaded joints.

Threads shall conform to ASME B 120.1. Pipe joint compound or tape shall be applied on the male threads only.

- 18-29-705.10.2  Mechanical joints.

Joints shall be made with an approved elastomeric seal. Mechanical joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-705.11  Deliberately omitted.

- 18-29-705.12  PVC plastic.

Joints between PVC plastic pipe or fittings shall comply with Sections 18-29-705.12.1 through 18-29-705.12.3.

- 18-29-705.12.1  Mechanical joints.

Mechanical joints on drainage pipe shall be made with an elastomeric seal conforming to ASTM C 1173, ASTM D 3212 or CSA CAN/CSA-B602. Mechanical joints shall not be installed in above-ground systems, unless otherwise approved. Joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-705.12.2  Solvent cementing.

Joint surfaces shall be clean and free from moisture. A purple primer that conforms to ASTM F 656 shall be applied. Solvent cement not purple in color and conforming to ASTM D 2564, CSA CAN/CSA-B 137.3, CSA CAN/CSA-B 181.2 or CSA CAN/CSA- B182.1 shall be applied to all joint surfaces. The joint shall be made while the cement is wet and shall be in accordance with ASTM D 2855. Solvent-cement joints shall be permitted above or below ground.

- 18-29-705.12.3  Threaded joints.

Threads shall conform to ASME B 1.20.1. Schedule 80 or heavier pipe shall be permitted to be threaded with dies specifically designed for plastic pipe. Approved thread lubricant or tape shall be applied on the male threads only.

- 18-29-705.13  Vitrified clay.

Joints between vitrified clay pipe or fittings shall be made with an elastomeric seal conforming to ASTM C 425, ASTM C 1173 or CSA CAN/CSA-B602.

- 18-29-705.14  Joints between different materials.

Joints between different piping materials shall be made with a mechanical joint of the compression or mechanical-sealing type, or as permitted in Sections 18-29-705.14.1 through 18-29-705.14.6. Connectors or adapters shall have an elastomeric seal conforming to ASTM C 425, ASTM C 443, ASTM C 564, ASTM C 1173, ASTM D 1869, ASTM F 477, CSA A2573 or CSA CAN/CSA B602. Joints shall be installed in accordance with the manufacturer's instructions.

- 18-29-705.14.1  Copper or copper-alloy tubing to cast-iron hub pipe.

Joints between copper or copper-alloy tubing and cast-iron hub pipe shall be made with a brass ferrule or compression joint. The copper or copper-alloy tubing shall be soldered to the ferrule in an approved manner, and the ferrule shall be joined to the cast-iron hub by a caulked joint or a mechanical no hub coupling.

- 18-29-705.14.2  Copper or copper-alloy tubing to galvanized steel pipe.

Joints between copper or copper-alloy tubing and galvanized steel pipe shall be made with a brass converter fitting or dielectric fitting. The copper tubing shall be soldered to the fitting in an approved manner, and the fitting shall be screwed to the threaded pipe.

- 18-29-705.14.3  Cast-iron pipe to galvanized steel or brass pipe.

Joints between cast-iron and galvanized steel or brass pipe shall be made by either caulked or threaded joints or with an approved adapter fitting.

- 18-29-705.14.4  Plastic pipe or tubing to other piping material.

Joints between different grades of plastic pipe or between plastic pipe and other piping material shall be made with an approved adapter fitting. Joints between plastic pipe and cast-iron hub pipe shall be made by a caulked joint or a mechanical compression joint.

- 18-29-705.14.5  Deliberately omitted.

- 18-29-705.14.6  Borosilicate glass to other materials.

Joints between glass pipe and other types of materials shall be made with adapters having a TFE seal and shall be installed in accordance with the manufacturer's instructions.

- 18-29-705.15  Drainage slip joints.

Slip joints shall be made with an approved elastomeric gasket and shall only be installed on the trap outlet, trap inlet and within the trap seal. Slip joints installed in concealed locations shall conform to Section 18-29-405.8.

- 18-29-705.16  Caulking ferrules.

Ferrules shall be of red brass and shall be in accordance with Table 18-29-705.16.

Table 18-29-705.16
Caulking Ferrule Specifications

Pipe Sizes (inches); Inside Diameter (inches); Length (inches); Minimum Weight Each. 2; 2 1/4; 4 1/2; 1 pound. 3; 3 1/4; 4 1/2; 1 pound 12 ounces. 4; 4 1/4; 4 1/2; 2 pounds 6 ounces.

For SI: 1 inch = 25.4 mm, 1 ounce = 28.35g, 1 pound = 0.454 kg

- 18-29-705.17  Deliberately omitted.

- 18-29-706  Connections Between Drainage Piping And Fixtures.

- 18-29-706.1  Connections and changes in direction.

All connections and changes in direction of the sanitary drainage system shall be made with approved drainage fittings. Connections between drainage piping and fixtures shall conform to Section 18-29-405.

- 18-29-706.2  Obstructions.

The fittings shall not have ledges, shoulders or reductions capable of retarding or obstructing flow in the piping. Threaded drainage pipe fittings shall be of the recessed drainage type.

- 18-29-706.3  Installation of fittings.

Fittings shall be installed to guide sewage and waste in the direction of flow. Change in direction shall be made by fittings installed in accordance with Table 18-29-706.3. Change in direction by combination fittings, side inlets or increasers shall be installed in accordance with Table 18-29-706.3 based on the pattern of flow created by the fitting. Double sanitary tee patterns shall not receive the discharge of back-to-back water closets and fixtures or appliances with pumping action discharge.

Table 18-29-706.3
Fittings for Change in Direction

Type of Fitting Pattern; Change in Direction. Horizontal to vertical; Vertical to horizontal; Horizontal to horizontal. Sixteenth bend; X; X; X. Eighth bend; X; X; X. Sixth bend; X; X; X. Quarter bend; X; X a; X a. Short sweep; X; X a, b; X a. Long sweep; X; X; X. Sanitary tee; X c; –; –. Wye; X; X; X. Combination wye and eight bend; X; X; X.

For SI: 1 inch = 25.4 mm.

a The fittings shall only be permitted for a 2-inch or smaller fixture drain.

b Three inches and larger.

c For a limitation on double sanitary tees, see Section 706.3.

- 18-29-707  Prohibited Joints and Connections.

- 18-29-707.1  Prohibited joints.

The following types of joints and connections shall be prohibited, unless approved by the sewers department guidelines or as referenced in the current edition of that department's permit requirement and fees:

1.     Cement or concrete joints;

2.     Mastic or hot-pour bituminous joints;

3.     Joints made with fittings not approved for the specific installation;

4.     Joints between different diameter pipes made with elastomeric rolling O-rings;

5.     Solvent-cement joints between different types of plastic pipe; and

6.     Saddle-type fittings.

- 18-29-708  Cleanouts.

- 18-29-708.1  Scope.

This section shall govern the size, location, installation and maintenance of drainage pipe cleanouts.

- 18-29-708.2  Cleanout plugs.

Cleanout plugs shall be of brass, plastic or other approved materials. Brass cleanout plugs shall be utilized with metallic drain, waste and vent piping only, and shall conform to ASTM A 74. Plastic cleanout plugs shall conform to the requirements of Section 18-29-702.4. Plugs shall have raised square or countersunk square heads. Countersunk heads shall be installed where raised heads are a trip hazard. Cleanout plugs with borosilicate glass systems shall be of borosilicate glass.

- 18-29-708.3  Where required.

Cleanouts shall be located in accordance with Sections 18-29-708.3.1 through 18-29-708.3.5.

- 18-29-708.3.1  Horizontal drains within buildings.

All horizontal drains shall be provided with cleanouts located not more than 100 feet (30.48m) apart, except that the maximum shall be 50 feet (15.25 m) for drains 4 inches (100 mm) diameter or less, 150 feet (45.7 m) for drains 10 inches (250 mm) diameter or larger.

- 18-29-708.3.2  Building sewers.

All building sewers shall be provided with cleanouts located not more than 100 feet (30.48 m) apart measured from the upstream entrance of the cleanout, unless manholes are adequately spaced according to the current edition of the permit requirement and fees book.

- 18-29-708.3.3  Changes of direction.

Cleanouts shall be installed at each change of direction of the building drain or horizontal waste or soil lines greater than 45 degrees (0.79 rad). Where more than one change of direction occurs in a run of piping, only one cleanout shall be required for each 40 feet (12.2 m) of developed length of the drainage piping.

- 18-29-708.3.4  Base of stack.

A cleanout shall be provided at the base of each waste or soil stack.

- 18-29-708.3.5  Building drain and building sewer junction.

There shall be a cleanout near the junction of the building drain and the building sewer. The cleanout shall be either inside or outside the building wall and shall be brought up to the finished ground level or to the basement floor level. An approved two-way cleanout is allowed to be used at this location to serve as a required cleanout for both the building drain and building sewer. The cleanout at the junction of the building drain and building sewer shall not be required if the cleanout on a 3-inch (75 mm) or larger diameter soil stack is located within a developed length of 10 feet (3.05 m) of the building drain and building sewer connection.

- 18-29-708.3.6  Manholes.

Manholes serving a building drain shall have secured gas-tight covers and shall be located in accordance with Section 18-29-708.8.

- 18-29-708.4  Concealed piping.

Cleanouts on concealed piping, piping under a floor slab or piping in a crawl space of less than 36 inches (915 mm) in height, or piping in a plenum shall be extended through and shall terminate flush with the finished wall, floor or ground surface or shall be extended to the outside of the building. Cleanout plugs shall not be covered with cement, plaster or any other permanent finish material. Where it is necessary to conceal a cleanout or to terminate a cleanout in an area subject to vehicular traffic, the covering plate, access door or cleanout shall be of an approved type designed and installed for this purpose.

- 18-29-708.5  Opening direction.

Every cleanout shall be installed to open to allow cleaning in the direction of the flow of the drainage pipe or at right angles thereto.

- 18-29-708.6  Prohibited installation.

Cleanout openings shall not be utilized for the installation of new fixtures or floor drains, except where approved and where another cleanout of equal access and capacity is provided.

- 18-29-708.7  Minimum size.

Cleanouts shall be the same nominal size as the pipe they serve up to 4 inches (100 mm). For pipes larger than 4 inches (100 mm) nominal size, the minimum size of the cleanout shall be 4 inches (100 mm).

Exception: “P” trap connections with slip joints or ground joint connections, or stack cleanouts that are no more than one pipe diameter smaller than the drain served, shall be approved.

- 18-29-708.8  Pipes 8 inches and larger.

For building sewers 8 inches (200 mm) and larger nominal size, manholes shall be provided and located at each change in direction greater than 45 degrees, and at the locations and intervals referenced in the current edition of the permit requirement and fees book.

- 18-29-708.9  Clearances.

Cleanouts on 6-inch (150 mm) and smaller pipes shall be provided with a clearance of not less than 18 inches (457 mm) for rodding. Cleanouts on 8-inch (200 mm) and larger pipes shall be provided with a clearance of not less than 36 inches (914 mm) for rodding.

- 18-29-708.10  Access.

Access shall be provided to all cleanouts.

- 18-29-709  Fixture Units.

- 18-29-709.1  Values for fixtures.

Drainage fixture unit values as given in Table 18-29-709.1 designate the relative load weight of different kinds of fixtures that shall be employed in estimating the total load carried by a soil or waste pipe, and shall be used in connection with Tables 18-29-710A and 18-29-710B of sizes for soil, waste and vent pipes for which the permissible load is given in terms of fixture units.

Table 18-29-709.1
Drainage Fixture Units for Fixtures and Groups

Fixture Type; Drainage Fixture Unit Value as Load Factors; Minimum Size of Trap (inches). Automatic clothes washers, commercial a; 3; 2. Automatic clothes washers, residential; 2; 2. Bathroom group consisting of water closet, lavatory, bidet and bathtub or shower; 6; –. Bathroom b (with or without overhead shower or whirlpool attachments); 2; 1 1/2. Bidet; 2; 1 1/4. Combination sink and tray; 2; 1 1/2. Dental lavatory; 1; 1 1/4. Dental unit or cuspidor; 1; 1 1/4. Dishwashing machine, c domestic; 2; 1 1/2. Drinking fountains; 1/2; 1 1/4. Emergency floor drain; 0; 2. Floor drains; 2; 2. Kitchen sink, domestic; 2; 1 1/2. Kitchen sink, domestic with food waste grinder and/or dishwasher; 2; 1 1/2. Laundry tray (1 or 2 compartments); 2; 1 1/2. Lavatory; 1; 1 1/4. Shower compartment, domestic; 2; 2. Sink; 2; 1 1/2. Urinal; 4; Footnote d. Urinal, 1 gallon per flush or less; 2 e; Footnote d. Wash sink, (circular or multiple) each set of faucets; 2; 1 1/2. Water closet, flushometer tank, public or private; 4 e; Footnote d. Water closet private installation; 4; Footnote d. Water closet public installation; 6; Footnote d.

For SI: 1 inch = 25.4 mm, 1 gallon = 3.785L.

a For traps larger than 3 inches, use Table 709.2.

b A showerhead over a bathtub or whirlpool bathtub attachments does not increase the drainage fixture unit value.

c See Section 709.2 for methods of computing unit value of fixtures not listed in Table 709.1 or for rating of devices with intermittent flows.

d Trap size shall be consistent with the fixture outlet size.

e For the purpose of computing loads on building drains and sewers, water closets or urinals shall not be rated at a lower drainage fixture unit unless the lower values are confirmed by testing.

- 18-29-709.2  Fixtures not listed in Table 18-29-709.1.

Fixtures not listed in Table 18-29-709.1 shall have a drainage fixture unit load based on the outlet size of the fixture in accordance with Table 18-29-709.2. The minimum trap size for unlisted fixtures shall be the size of the drainage outlet but not less than 1 1/4 inches (32 mm).

Table 18-29-709.2
Drainage Fixture Units for Fixture Drains or Traps

Fixture Drain or Trap Size (inches); Drainage Fixture Unit Value. 1 1/4; 1. 1 1/2; 2. 2; 3. 2 1/2; 4. 3; 5. 4; 6.

For SI: 1 inch = 25.4 mm.

- 18-29-709.3  Values for continuous flow.

Drainage fixture unit values for continuous flow into a drainage system shall be computed on the basis that 1 gallon per minute (0.06 L/s) of flow is equivalent to one fixture unit.

- 18-29-709.4  Deliberately omitted.

- 18-29-709.5  Values for indirect waste receptor.

The drainage fixture unit load of an indirect waste receptor receiving the discharge of indirectly connected fixtures shall be the sum of the drainage fixture unit values of the fixtures that discharge to the receptor. If this drainage fixture value is less than the indirect waste receptor drainage fixture value given in Table 18-29-709.1 or Table 18-29-709.2, then the values in the referenced tables shall be used.

- 18-29-710  Drainage System Sizing.

- 18-29-710.1  Maximum fixture unit load.

The maximum number of drainage fixture units connected to a given size of building sewer, building drain or horizontal branch of the building drain shall be determined using Table 18-29-710A. The maximum number of drainage fixture units connected to a given size of horizontal branch or vertical soil or waste stack shall be determined using Table 18-29-710B.

- 18-29-710.1.1  Maximum fixture units.

The maximum number of fixture units that may be connected to a given size of house drain, horizontal branch, or vertical soil or waste stack is given in Tables 18-29-710A and 18-29-710B. Storm and combined house drains and house sewers shall comply with Sections 18-29-1106 and 18-29-1108 of this chapter.

- 18-29-710.1.2  Minimum size.

The minimum required pipe size for water closets or pedestal urinal branches and stacks shall be 4 inches (100 mm) except that any building three stories or less in height and used exclusively for family unit occupancy, may utilize a 3-inch (75 mm) soil stack when not exceeding 30 fixture units, with not more than two water closets per floor or two water closets per horizontal branch. The waste connection to any water closet shall be provided with an approved 4-inch (100 mm) closet flange. The minimum required sizes for underground branches from downspouts, floor drains, laundry trays and sink stacks shall be 3 inches (75 mm). (See Tables 18-29-710A and 18-29-710B.)

- 18-29-710.1.3  Horizontal stack offsets.

Horizontal stack offsets shall be sized as required for building drains in accordance with Table 18-29-710A, except as required by Section 18-29-711.4.

- 18-29-710.1.4  Vertical stack offsets.

Vertical stack offsets shall be sized as required for straight stacks in accordance with Table 18-29-710B, except when required to be sized as a building drain in accordance with Section 18-29-711.1.

- 18-29-710.2  Future fixtures.

When provision is made for the future installation of fixtures, those provided for shall be considered in determining the required sizes of drain pipes. Construction to provide for such future installation shall be terminated with an approved cap or plug.

- 18-29-710.3  Underground drainage piping.

Any portion of the drainage system installed underground or below a basement or cellar shall not be less than 4 inches (100 mm) in diameter.

Table 18-29-710A
Building Drains and Sewers

Diameter of Pipe (inches); Maximum Number of Drainage Fixture Units Connected to any Portion of the Building Drain or the Building Sewer, Including Branches of the Building Drain a. Slope per Foot. 1/6 inch; 1/8 inch; 1/4 inch; 1/2 inch. 1 1/4; –; –; 1; 1. 1 1/2; –; –; 3; 3. 2; –; –; 21; 26. 2 1/2; –; –; 24; 31. 3; –; 36; 42; 50. 4; –; 180; 216; 250. 5; –; 390; 480; 575. 6; –; 700; 840; 1,000. 8; 1,400; 1,600; 1,920; 2,300. 10; 2,500; 2,900; 3,500; 4,200. 12; 2,900; 4,600; 5,600; 6,700. 15; 7,000; 8,300; 10,000; 12,000.

For SI: 1 inch = 25.4 mm, 1 inch per foot = 0.0833 mm/m.

a The minimum size of any building drain serving a water closet shall be 3 inches.

Table 18-29-710B
Horizontal Fixture Branches and Stacks a

Diameter of Pipe (inches); Any Horizontal Fixture Branch; Maximum Number of Fixture Units that may be Connected to:. One Stack of 3 Stories in Height or 3 Intervals; More than 3 Stories in Height. Total for Stack; Total at One Story or Branch Interval. 1 1/2; 3; 4; 8; 2. 2; 6; 10; 24; 6. 2 1/2; 12; 20; 42; 9. 3; 20; 30; 60; 16. 4; 160; 240; 500; 90. 5; 360; 540; 1,100; 200. 6; 620; 960; 1,900; 350. 8; 1,400; 2,200; 3,600; 600. 10; 2,500; 3,800; 5,600; 1,000. 12; 3,900; 6,000; 8,400; 1,500. 15; 7,000; –; –; –.

For SI: 1 inch = 25.4 mm.

a Does not include branches of house drain.

- 18-29-711  Offsets in Drainage Piping in Buildings of Five Stories or More.

- 18-29-711.1  Horizontal branch connections above or below vertical stack offsets.

If a horizontal branch connects to the stack within 2 feet (610 mm) above or below a vertical stack offset, and the offset is located more than four branch intervals below the top of the stack, the offset shall be vented in accordance with Section 18-29-915.

- 18-29-711.1.1  Omission of vents for vertical stack offsets.

Vents for vertical offsets required by Section 18-29-711.1 shall not be required where the stack and its offset are sized as a building drain (see Table 18-29-710A, Column 5).

- 18-29-711.2  Horizontal branch connections to horizontal stack offsets.

When a horizontal stack offset is located more than four branch intervals below the top of the stack, a horizontal branch shall not connect within the horizontal stack offset or within 2 feet (610 mm) above or below such offset.

- 18-29-711.3  Horizontal stack offsets.

A stack with a horizontal offset located more than four branch intervals below the top of the stack shall be vented in accordance with Section 914 and sized as follows:

1.     The portion of the stack above the offset shall be sized as for a vertical stack based on the total number of drainage fixture units above the offset.

2.     The offset shall be sized in accordance with Section 18-29-710.1.1.

3.     The portion of the stack below the offset shall be sized as for the offset or based on the total number of drainage fixture units on the entire stack, whichever is larger (see Table 18-29-710B, Column 4).

- 18-29-711.3.1  Omission of vents for horizontal stack offsets.

Vents for horizontal stack offsets required by Section 18-29-711.3 shall not be required where the stack and its offset is one pipe size larger than required for a building drain (see Table 18-29-710A, Column 5) and the entire stack and offset is not less in cross- sectional area than that required for a straight stack plus the area of an offset vent as provided for in Section 18-29-915. Omission of offset vents in accordance with this section shall not constitute approval of horizontal branch connections within the offset or within 2 feet (610 mm) above or below the offset.

- 18-29-711.3.2  Suds pressure zones.

Drainage stacks that receive wastes from sinks, automatic dishwashers, laundry trays, laundry washing machines, and similar fixtures shall have the drainage and vent piping so arranged that suds pressures will not affect fixtures in the lower portion of the drainage system. No fixture drain, branch, or branch vent shall connect to any stack in a suds pressure zone. Such zones shall be considered to exist at any offset of 60 degrees to 90 degrees or at the base of any drainage.

- 18-29-711.3.2.1  Height.

When the drainage portion of a stack exceeds 16 feet (4.88 m) in height above a 45-degree to 90-degree offset or house drain, it shall have its lower portion consisting of 30 percent of its height from such offset free of any fixture drain or branch. Such suds pressure zone of the drainage stack need not exceed 24 feet (7.32 m) in height.

- 18-29-711.3.2.2  Upstream.

In an offset of 60 degrees to 90 degrees or a house drain when the drainage portion of a stack exceeds 16 feet (4.88 m) in height, a zone in the horizontal piping consisting of 30 percent upstream of the drainage stack connection shall be free of any drainage openings. Such suds pressure zone of the offset or house drain need not exceed 24 feet (7.32 m).

- 18-29-711.3.2.3  Downstream.

In an offset of 60 degrees to 90 degrees or a house drain when the drainage portion of a stack exceeds 16 feet (4.88 m) in height, a zone in the horizontal piping consisting of 15 percent downstream of the drainage stack connection shall be free of any drainage openings. Such suds pressure zone of the offset or house drain need not exceed 12 feet (3.66 m).

- 18-29-711.4  Offsets below lowest branch.

Where a vertical offset occurs in a soil or waste stack below the lowest horizontal branch, change in diameter of the stack because of the offset shall not be required. If a horizontal offset occurs in a soil or waste stack below the lowest horizontal branch, the required diameter of the offset and the stack below it shall be determined as for a building drain in accordance with Table 18-29-710A.

- 18-29-712  Sumps and Ejectors.

- 18-29-712.1  Building drains below sewer.

Building drains that cannot be discharged to the sewer by gravity flow shall be discharged into a tightly covered and vented sump, from which stack the liquid shall be lifted and discharged into the building gravity drainage system by automatic pumping equipment or other approved method.

- 18-29-712.2  Check and gate valve required.

A gate valve located on the discharge side of the check valve shall be installed in the pump or ejector discharge piping between the pump or ejector and the gravity drainage system. Access shall be provided to such valves. Such valves shall be located above the sump cover required by Section 18-29-712.1 or, when the discharge pipe from the ejector is below grade, the valves shall be accessibly located outside the sump below grade in an access pit with a removable access cover.

Exception: In single family residential buildings, only a check valve shall be required, located on the discharge piping from the sewage pump or ejector.

- 18-29-712.3  Sump design.

The sump pump, pit and discharge piping shall conform to the requirements of Sections 18-29-712.3.1 through 18-29-712.3.5.

- 18-29-712.3.1  Sump pump.

The sump pump capacity and head shall be appropriate to anticipated use requirements.

- 18-29-712.3.2  Sump pit.

The sump pit shall be not less than 18 inches (457 mm) in diameter and 30 inches (762 mm) deep, unless otherwise approved. The pit shall be accessible and located such that all drainage flows into the pit by gravity. An approved sump pit or tank within a building receiving the discharge from sanitary drains, storm water or combined drains shall be constructed of steel, cast iron, reinforced concrete pipe or other approved materials. The sump or tank receiving the discharge from subsurface soil drainage shall be constructed of vitrified clay tile or any of the above materials. Approved plastic or fiberglass liners may be used in conjunction with any of the approved materials referenced above. The pit bottom shall be solid and provide permanent support for the pump. The sump pit shall be fitted with a gas-tight removable cover adequate to support anticipated loads in the area of use. The sump pit receiving sanitary flow shall be vented in accordance with Article 18-29-9.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-712.3.3  Discharge piping.

Discharge piping shall meet the requirements of Section 18-29-712.2.

- 18-29-712.3.4  Maximum effluent level.

The effluent level control shall be adjusted and maintained to at all times prevent the effluent in the sump from rising to within 2 inches (50 mm) of the invert of the gravity drain inlet into the sump.

- 18-29-712.3.5  Ejector connection to the drainage system.

Pumps connected to the drainage system shall connect to the building sewer or shall connect to a wye fitting in the building drain a minimum of 10 feet (3.05 mm) from the base of any soil stack, waste stack or fixture drain. Where the discharge line connects into horizontal drainage piping, the connector shall be made through a wye fitting into the top of the drainage piping.

- 18-29-712.4  Sewage pumps and sewage ejectors.

A sewage pump or sewage ejector shall automatically discharge the contents of the sump to the building drainage system.

- 18-29-712.4.1  Capacity.

A sewage pump or sewage ejector shall have the capacity and head for the application requirements. Pumps or ejectors that receive the discharge of water closets shall be capable of handling spherical solids with a diameter of up to and including 2 inches (50 mm). Other pumps or ejectors shall be capable of handling spherical solids with a diameter of up to and including 1 inch (25 mm). The minimum capacity of a pump or ejector based on the diameter of the discharge pipe shall be in accordance with Table 18-29-712.4.1.

Exception: Grinder pumps or grinder ejectors that receive the discharge of water closets shall have a minimum discharge opening of 1 1/4 inches (32 mm).

Table 18-29-712.4.1
Minimum Capacity of Sewage Pump or Sewage Ejector

Diameter of the Discharge Pipe (inches); Capacity of Pump or Ejector (gpm). 2; 21. 2 1/2; 30. 3; 46.

For SI: 1 inch = 25.4 mm, 1 gpm = 3.785 L/m.

- 18-29-712.4.2  Duplex equipment required.

Where six or more water closets are connected to a sewage ejector, the system shall incorporate duplex pumping equipment.

- 18-29-713  Health Care Plumbing.

- 18-29-713.1  Scope.

Sections 18-29-713.1 through 18-29-713.11.4 shall govern those aspects of health care plumbing systems that differ from plumbing systems in other structures. Health care plumbing systems shall conform to these sections in addition to the other requirements of this chapter. These sections shall apply to the special devices and equipment installed and maintained in the following occupancies: nursing homes, homes for the aged, orphanages, infirmaries, first aid stations, psychiatric facilities, clinics, professional offices of dentists and doctors, mortuaries, educational facilities, surgery, dentistry, research and testing laboratories, establishments manufacturing pharmaceutical drugs and medicines, and other structures with similar apparatus and equipment classified as plumbing.

- 18-29-713.2  Bedpan washers and clinical sinks.

Bedpan washers and clinical sinks shall connect to the drainage and vent system in accordance with the requirements for a water closet. Bedpan washers shall also connect to a local vent.

- 18-29-713.3  Indirect waste.

All sterilizers, steamers and condensers shall discharge to the drainage through an indirect waste pipe by means of an air gap. Where a battery of not more than three sterilizers discharges to an individual receptor, the distance between the receptor and a sterilizer shall not exceed 8 feet (2438 mm). The indirect waste pipe on a bedpan steamer shall be trapped.

- 18-29-713.4  Vacuum system station.

Ready access shall be provided to vacuum system station receptacles. Such receptacles shall be built into cabinets or recesses and shall be visible.

- 18-29-713.5  Bottle system.

Vacuum (fluid motion) systems intended for collection, moving and disposing of blood, pus or other fluids by the bottle system shall be provided with receptacles equipped with an overflow prevention device at each vacuum outlet station.

- 18-29-713.6  Central disposal system equipment.

All central vacuum (fluid suction) systems shall provide continuous service systems equipped with collecting or control tanks shall provide for draining and cleaning of the tanks while the system is in operation. In hospitals, the system shall be connected to the emergency power system. The exhausts from a vacuum pump serving a vacuum (fluid suction) system shall discharge separately to open air above the roof.

- 18-29-713.7  Central vacuum or disposal systems.

Where the waste from a central vacuum (fluid suction) system of the barometric-lag, collection-tank or bottle-disposal type is connected to the drainage system, the waste shall be directly connected to the sanitary drainage system through a trapped waste.

- 18-29-713.7.1  Piping.

The piping of a central vacuum (fluid suction) system shall be of corrosion-resistant material with a smooth interior surface. A branch shall not be less than 1/2 inch (12 mm) nominal pipe size for one outlet and shall be sized in accordance with the number of vacuum outlets. A main shall not be less than 1 inch (25 mm) nominal pipe size. The pipe sizing shall be increased in accordance with the manufacturer's instructions as stations are increased. For the purposes of inspection, maintenance and replacement, all piping shall have cleanout facilities on mains and branches. Access shall be provided to such cleanout facilities.

- 18-29-713.7.2  Velocity.

The velocity of airflow in a central vacuum (fluid suction) system shall be less than 5,000 feet per minute (25.4 m/s).

- 18-29-713.8  Vent connections prohibited.

Connections between local vents serving bedpan washers or sterilizer vents serving sterilizing apparatus and normal sanitary plumbing systems are prohibited. Only one type of apparatus shall be served by a local vent.

- 18-29-713.9  Local vents and stacks for bedpan washers.

Bedpan washers shall be vented to open air above the roof by means of one or more local vents. The local vent for a bedpan washer shall not be less than a 2-inch-diameter (50 mm) pipe. A local vent serving a single bedpan washer is permitted to drain to the fixture served.

- 18-29-713.9.1  Multiple installations.

Where bedpan washers are located above each other on more than one floor, a local vent stack is permitted to be installed to receive the local vent on the various floors. Not more than three bedpan washers shall be connected to a 2-inch (50 mm) local vent stack, not more than six to a 3-inch (75 mm) local vent stack and not more than 12 inch (305 mm) to a 4-inch (100 mm) local vent stack.* In multiple installations, the connections between a bedpan washer local vent and a local vent stack shall be made with tee or tee-wye sanitary pattern drainage fittings installed in an upright position.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “...not more than 12 to a 4-inch (100 mm) local vent stack.”

- 18-29-713.9.2  Trap required.

The bottom of the local vent stack, except where serving only one bedpan washer, shall be drained by means of a trapped and vented waste connection to the sanitary drainage system. The trap and waste shall be the same size as the local vent stack.

- 18-29-713.9.3  Trap seal maintenance.

A water supply pipe not less than 1/4 inch (6 mm) in diameter shall be taken from the flush supply of each bedpan washer on the discharge or fixture side of the vacuum breaker, shall be trapped to form not less than a 3-inch (75 mm) water seal, and shall be connected to the local vent stack on each floor. The water supply shall be installed so as to provide a supply of water to the local vent stack for cleansing and drain trap seal maintenance each time a bedpan washer is flushed.

- 18-29-713.10  Sterilizer vents and stacks.

Multiple installations of pressure and non-pressure sterilizers shall have the vent connections to the sterilizer vent stack made by means of inverted wye fittings. Access shall be provided to vent connections for the purpose of inspection and maintenance.

- 18-29-713.10.1  Drainage.

The connection between sterilizer vent or exhaust openings and the sterilizer vent stack shall be designed and installed to drain to the funnel or basket-type waste fitting. In multiple installations, the sterilizer vent stack shall be drained separately to the lowest sterilizer funnel or basket-type waste fitting or receptor.

- 18-29-713.11  Sterilizer vent stack sizes.

Sterilizer vent stack sizes shall comply with Section 18-29-713.11.1 through Section 18-29-713.11.4.

- 18-29-713.11.1  Bedpan steamers.

The minimum size of a sterilizer vent serving a bedpan steamer shall be 1 1/2 inches (38 mm) in diameter. Multiple installations shall be sized in accordance with Table 18-29-713.11.1.

Table 18-29-713.11.1
Stack Sizes for Bedpan Steamers and Boiling Type Sterilizers (Number of Connections of Various 
Sizes Permitted to Various-Sized Sterilizer Vent Stacks)

Stack Size (inches); Connection Size. 1 1/2"; 2". 1 1/2 a; 1; or; 0. 2 a; 2; or; 1. 2 b; 1; or; 1. 3 a; 4; or; 2. 3 b; 2; or; 2. 4 a; 8; or; 4. 4 b; 4; or; 4.

For SI: 1 inch = 25.4 mm

a Total of each size.

b Combination of sizes.

- 18-29-713.11.2  Boiling-type sterilizers.

The minimum size of a sterilizer vent stack shall be 2 inches (51 mm) in diameter where serving a utensil sterilizer and 1 1/2 inches (38 mm) in diameter where serving an instrument sterilizer. Combinations of boiling-type sterilizer vent connections shall be sized in accordance with Table 18-29-713.11.1.

- 18-29-713.11.3  Pressure sterilizers.

Pressure sterilizer vent stacks shall be 2 1/2 inches (64 mm) minimum. Those serving combinations of pressure sterilizer exhaust connections shall be sized in accordance with Table 18-29-713.11.3.

Table 18-29-713.11.3
Stacks Sizes for Pressure Sterilizers (Number of Connections of Various 
Sizes Permitted to Various- Sized Vent Stacks)

Stack Size (inches); Connection Size. 3/4"; 1"; 1 1/4"; 1 1/2". 1 1/2a; 3 or; 2 or; 1; –. 1 1/2b; 2 and; 1; –; –. 2a; 6 or; 3 or; 2 or; 1. 2b; 3 and; 2; –; –. 2b; 2 and; 1 and; 1; –. 2b; 1 and; 1 and; –; 1. 3a; 15 or; 7 or; 5 or; 3. 3b; 1 and; 1 and 5 and; 2 and; 2 1.

For SI: 1 inch = 25.4 mm

a Total of each size.

b Combination of sizes.

- 18-29-713.11.4  Pressure instrument washer sterilizer sizes.

The minimum diameter of a sterilizer vent stack serving an instrument washer sterilizer shall be 2 inches (50 mm). Not more than two sterilizers shall be installed on a 2-inch (50 mm) stack, and not more than four sterilizers shall be installed on a 3-inch (75 mm) stack.

- 18-29-714  Deliberately omitted.

- 18-29-715  Backwater Valves.

- 18-29-715.1  Sewage backflow.

A backwater valve shall be installed only for plumbing fixtures where the overflow rim of the lowest plumbing fixtures are below the next upstream manhole in the public sewer. Plumbing fixtures with flood rims above the next upstream manhole shall not discharge through the backwater valve.

- 18-29-715.2  Fixture branches.

Backwater valves shall be installed in the branch of the building drain that receives only the discharge from fixtures located within such branch and shall be located below ground.

- 18-29-715.3  Material.

All bearing parts of backwater valves shall be of corrosion-resistant material. Backwater valves shall comply with ASME A112.14.1, CSA CAN/CSA-B 181.1 or CSA CAN/CSA-B 181.2.

- 18-29-715.4  Seal.

Backwater valves shall be so constructed as to provide a mechanical seal against backflow.

- 18-29-715.5  Diameter.

Backwater valves, when fully opened, shall have a capacity not less than that of the pipes in which they are installed.

- 18-29-715.6  Location.

Backwater valves shall be installed so that access is provided to the working parts for service and repair.

- 18-29-716  Flood Control.

- 18-29-716.1  Flood control devices.

Flood control devices in any house drain shall be vented and sized in accordance with this chapter. The total fixture units and any continuous or semicontinuous flow shall determine the size of the vent. No vent shall be less than 2 inches (50 mm) in diameter.

- 18-29-716.2  Flood control systems.

Flood control systems may be installed as necessary with the approval of the commissioner of sewers. Ground floor plumbing fixtures may discharge into the building sewage ejector, in areas experiencing sewer backup only when all downspouts or other storm drainage is discharging downstream of the backwater valve or when the downspouts are not connected to the sewer system.

- Article 8.  Indirect/Special Waste

- 18-29-801  General.

- 18-29-801.1  Scope.

This article shall govern matters concerning indirect waste piping and special wastes. This article shall further control matters concerning food handling establishments, sterilizers, clear-water wastes, swimming pools, methods of providing air breaks or air gaps, and neutralizing devices for corrosive wastes.

- 18-29-801.2  Protection.

All devices, appurtenances, appliances and apparatus intended to serve some special function, such as sterilization, distillation, processing, cooling, or storage of ice or foods, and that discharge to the drainage system, shall be provided with protection against backflow, flooding, fouling, contamination and stoppage of the drain.

- 18-29-802  Indirect Wastes.

- 18-29-802.1  Where required.

Indirect sanitary wastes shall be installed as follows: Waste piping from filters, refrigerators, ice boxes, steam tables, egg boilers, coffee makers, bottleholders, ice cube containers, or any equipment or other receptacle where food or drink is stored shall discharge to the drainage piping system through an air gap into a waste receptor. The minimum size shall be 1 inch (25 mm) and the maximum length of the indirect waste shall not exceed 15 feet (4.57 m) and shall be provided with cleanouts at every 90 degree turn and shall be accessibly located. Indirect wastes shall be piped to the waste receptor with material that is required by this chapter. Waste receptors serving indirect pipes connected to equipment shall not be installed in any toilet room, closet, store room or any inaccessible space. Each waste receptor shall be trapped and vented as required by this chapter. The air gap shall not be less than 1 inch.

- 18-29-802.1.1  Deliberately omitted.

- 18-29-802.1.2  Deliberately omitted.

- 18-29-802.1.3  Potable clear-water waste.

Where devices and equipment, such as sterilizers, swimming pools and relief valves, discharge potable water to the building drainage system, the discharge shall be through an indirect waste pipe by means of an air gap.

- 18-29-802.1.4  Nonpotable clear-water waste.

Where devices and equipment, such as safe pans, drip pans, process tanks, filters, drips and boilers, discharge nonpotable water to the building drainage system, the discharge shall be through an indirect waste pipe by means of an air break or an air gap.

- 18-29-802.1.5  Waste piping.

Waste piping from aspirators, sterilizers or any other equipment which would produce a partial vacuum by cooling shall discharge to the drainage piping system through an air gap into a waste receptor. The minimum size shall be 1 inch (25 mm) and the maximum length of the indirect waste shall not exceed 15 feet (4.57 m) and shall be provided with cleanouts at every 90 degree turn which are accessibly located. Each indirect waste pipe shall be individually piped to the waste receptor with material that is required by this chapter. Waste receptors serving indirect pipes connected to the above equipment shall be located in the same room. Each waste receptor shall be trapped and vented as required by this chapter. The air gap shall be not less than two times the diameter of the indirect waste pipe.

- 18-29-802.1.6  Dishwashing machine.

Dishwashing machines shall be indirectly connected, except when located adjacent to a floor drain, whereby the waste may be connected directly on the sewer side of the floor drain trap, and the fixture shall be trapped and vented as required by this chapter; provided, however, that no other waste or soil drainage line be permitted between the floor drain waste connection and the fixture drain. All indirectly connected dishwashing machine wastes shall be provided with a vented trap located as close as possible to the dishwashing machine and in the same room. The air gap shall not be less than 1 inch (25 mm).

- 18-29-802.1.7  Sinks.

Commercial dishwashing sinks, pot washing sinks, pre-rinse sinks, silverware sinks, bar sinks, soda fountain sinks, and other similar fixtures shall be indirectly connected except when located adjacent to a floor drain, whereby the waste may be connected directly on the sewer side of the floor drain trap, and the fixture shall be trapped and vented as required by this chapter; provided, however, that no other drainage line be permitted between the floor drain waste connection and the fixture drain. All indirectly connected sinks shall be provided with a vented trap located as close as possible to the sink and in the same room. The piping from the equipment to the air gap shall not exceed 5 feet (1,525 mm) and shall be of material as required by this chapter. The air gap shall be a minimum of 1 inch (25 mm).

- 18-29-802.2  Deliberately omitted.

- 18-29-802.3  Waste receptors.

Every waste receptor shall be of an approved type.

- 18-29-802.3.1  Open hub waste receptors.

Waste receptors shall be permitted in the form of a hub or pipe extending not less than 1 inch (25 mm) above a water-impervious floor and are not required to have a strainer.

- 18-29-802.4  Standpipes.

Standpipes shall be individually trapped. Standpipes shall extend a minimum of 18 inches (457 mm) and a maximum of 42 inches (1,066 mm) above the trap. Access shall be provided to all standpipe and drains for rodding.

- 18-29-803  Special Wastes.

- 18-29-803.1  Deliberately omitted.

- 18-29-803.2  Neutralizing device required for corrosive wastes.

Corrosive liquids, spent acids or other harmful chemicals that destroy or injure a drain, sewer, soil or waste pipe, or create noxious or toxic fumes or interfere with sewage treatment processes, shall not be discharged into the plumbing system device for corrosive waste. No corrosive wastes which are equal or greater in corrosive action than a ph lower than 4.5 or higher than 10.0, having corrosive properties sufficient to cause damage or hazards to structures, equipment, or personnel, shall discharge into any house sewer without first discharging into a dilution tank or basin. Such devices shall be automatically provided with a sufficient supply of diluting water or neutralizing medium so as to make the contents noninjurious before discharge into the drainage system. No other waste pipe shall connect to a dilution basin. Every dilution tank used for this purpose shall be constructed of earthenware, polyethylene, propylene or glass and shall be provided with a standing waste and overflow or other approved means to insure dilution.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-803.3  System design.

A chemical drainage vent system shall be designed and installed in accordance with this chapter. Chemical drainage and vent systems shall be completely separated from the sanitary systems. Chemical waste shall not discharge to a sanitary drainage system until such waste has been treated in accordance with Section 18-29-803.2.

- 18-29-803.4  Volatile wastes.

Gasoline, benzene, naphtha, and other volatile, flammable or explosive wastes shall not discharge into a house sewer, public sewer, or sewage treatment plant. Refer to Sections 18-29-1003.1 through 1003.13, Interceptors and Separators for oil interceptor requirements.

- 18-29-804  Materials, Joints and Connections.

- 18-29-804.1  General.

The materials and methods utilized for the construction and installation of indirect waste pipes and systems shall comply with the applicable provisions of Article 7.

- 18-29-804.2  Acid waste piping material.

Material for acid drainage waste and vents in Article 7 shall be specifically indicated and approved for acid waste drainage.

- 18-29-805  Waste Water Control.

- 18-29-805.1  Preliminary treatment.

Whenever an industrial plant or other establishment discharges or proposes to discharge industrial wastes into any waters, sewer, drain, watercourse or natural outlet in the city of Chicago, such plant or establishment shall either:

1.     Reduce or modify the objectionable characteristics or constituents of such industrial wastes to meet the limits or requirements of Section 18-29-805.2 and to prevent pollution; or

2.     Control the quantities and rates of discharge of such industrial wastes over a 24-hour day and a seven- day week to prevent surge discharges which may place an unreasonable burden upon the sewage works on the metropolitan water reclamation district.

- 18-29-805.1.1  Approval.

The commissioner of sewers shall require the owner, operator or tenant of such industrial plant or establishment to provide adequate preliminary treatment or handling facilities to accomplish such a result. Before any permit for the construction of preliminary treatment or handling facilities is issued, plans, specifications and other pertinent data or information relating to such proposed treatment or handling facilities shall be submitted for the approval of said commissioner. No permit shall be issued and no construction of such facilities shall be commenced without the prior written approval of said commissioner; and no substantial alteration or addition to or in the sewer or drain or in the preliminary treatment or handling facilities shall be made without the prior written approval of said commissioner.

- 18-29-805.2  Prohibited wastes.

No person shall discharge or cause to be discharged any of the wastes or waters described in Sections 18-29-805.2.1 and 18-29-805.2.2 into any sewer, watercourse, natural outlet or waters within or partially within or adjoining the boundaries of the city of Chicago.

- 18-29-805.2.1  Maximum concentration.

Maximum concentration acceptable for discharge into the sewage system of the city of Chicago shall be in accordance with that set forth by the metropolitan water reclamation district ordinance titled the sewage and waste control ordinance enacted September 18, 1969 and as amended from time to time.

- 18-29-805.2.2  Types of discharge.

Any discharge of wastes or water into a sewer which terminates in or is a part of the sewage system of the city of Chicago must not contain the following:

1.     Water or wastes containing more than 100 parts per million (833 pounds per million gallons; 378 kg. per 3,785,400 L) of fats, oils or greases if such water or wastes are in the opinion of the commissioner of sewers sufficient to:

1.     Interfere with the biological process of a sewage treatment plant;

2.     Interfere with proper operation of the sewage works; or

3.     Cause obstruction to flow in sewers; or cause pollution as herein defined;

2.     Liquids, solids or gases which by reason of their nature or quantity are sufficient to cause fire or explosion or be injurious in any way to the structures making up the sewage works or to the operation of the sewage works;

3.     Noxious or malodorous liquids, gases or substances which whether singly or by interactions with other wastes are sufficient to create a public nuisance or hazard to life sufficient to prevent entry into the sewers for their maintenance and repair;

4.     Water or wastes containing toxic substances in quantities which are sufficient to pose a hazard to life or interfere with the biological processes of the sewage treatment works;

5.     Garbage that has not been ground or comminuted to such a degree that all particles will be carried freely in suspension under conditions normally prevailing in public sewers with no particle greater than 1/2 inch (13 mm) in dimension;

6.     Radioactive wastes unless they comply with the Atomic Energy Commission Act of 1954 (68 Stat. 919 as amended and Part 20 Subpart D – Waste Disposal, Section 20.303 of the regulations issued by the Atomic Energy Commission) or amendments thereto;

7.     Solid or viscous wastes which cause obstruction to flow in sewers or other interference with the proper operation of the sewage system or sewage treatment works, such as grease, uncomminuted garbage, animal guts or tissues, paunch manure, bone, hair, hides, fleshings, entrails, feathers, sand, cinders, ashes, spent lime, stone or marble dust, metal, glass, straw, shavings, grass clippings, rags, spent grain, waste paper, wood, plastic, gas, tar, asphalt, residues, residues from refining processing of fuels or lubricating oil, gasoline, naptha and similar substances;

8.     Liquids or vapors having a temperature higher than 150°F (65.7°C) at point of entrance into a public sewer;

9.     Waters or waste containing substances which are not amenable to treatment or reduction by the sewage treatment process employed or are amenable to treatment only to such degree that the water reclamation plants effluent cannot meet the requirement of other agencies having jurisdiction of discharge to the receiving waters;

10.     Excessive discoloration (such as – but not limited to – dye waste and vegetable tanning solutions); or

11.     Hg. concentration of mercury, Hg shall not exceed the standards set forth in the Illinois Pollution Control Board's Mercury Regulation No. R70-5; adopted March 31, 1971.

- 18-29-805.3  Discharges of clean waters.

Wherever possible clean waters from air conditioning, cooling or condensing systems or from swimming pools or cleaning waters resulting from pretreatment of industrial wastes shall be discharged into a storm sewer, combined sewer or natural outlet approved by the commissioner of sewers.

- 18-29-805.4  Manholes.

Any person discharging industrial wastes into a sewer shall construct and maintain a suitable control manhole or manholes downstream from any such places of discharge to permit observation, measurement and sampling of such wastes by the department of sewers or by personnel of the metropolitan water reclamation district. Where no manhole has been constructed or can be constructed, as in the case of some existing industries, the control manhole shall be considered to be the nearest downstream manhole in the public sewer to the point at which the building sewer is connected.

- 18-29-805.4.1  Use and permit.

The use of manholes shall be determined by the metropolitan water reclamation district and the department of sewers. The department of sewers will require a permit for the repair, adjustment, construction or cleaning of sewers or sewer structures.

- 18-29-805.5  Gauging and sampling.

The commissioner of sewers shall have the right to enter and set up, on the owner's property, such devices as may be necessary to conduct a gauging and sampling operation after first giving 10 days advance notice of his intention so to do. While performing said gauging and sampling, said commissioner, his representative or anyone performing said work in his behalf, shall observe and comply with all safety rules applicable to the premises, established by the said owner or occupant.

- 18-29-805.5.1  Legal or financial obligation.

The commissioner of sewers is hereby authorize to make arrangement with the metropolitan water reclamation district without incurring any legal or financial obligation upon the city of Chicago, to undertake and conduct such gauging and sampling operations, in its behalf; and to provide the necessary devices and facilities as well as the personnel and also to make the analyses of samples of such wastes, as hereinafter provided, in its own laboratories and other facilities or equipment; provided, that no such arrangements with the District shall place any personnel of the District under the control of said commissioner or cause such personnel of the district to be treated as employees of the city of Chicago for any purposes whatsoever.

- 18-29-805.6  Sampling methods.

In order to ascertain whether or not the sewage or waste of any kind discharged by any person into any waters or sewage system conforms to the criteria or water quality standards of the environment department of the building department of sewers will use any appropriate method or device which will lead to such a determination.

- 18-29-805.7  Analyses.

All analyses to determine the strength and character of industrial wastes shall be made in accordance with the latest edition of “Standard Methods for Examination of Water and Waste Water” prepared and published jointly by the American Public Health Association, American Water Works Association and Water Pollution Control Federation. Strength, character and quantity of wastes shall be based on any appropriate samples taken from the flow from all plant outlets discharging into a single public sewer.

- 18-29-805.7.1  Preliminary treatment.

The building commissioner shall require the owner, operator or tenant of such industrial plant or other establishment to provide adequate preliminary treatment of handling facilities to accomplish such a result. Before any permit for the construction of preliminary treatment of handling facilities shall be issued, plans, specifications and other pertinent data or information relating to such proposed treatment or handling facilities shall be submitted by the industry for approval of said commissioner, and no construction of such facilities shall be commenced without the prior written approval of said commissioner and no substantial alteration or addition to or in the sewer or drain or in the preliminary treatment or handling facilities shall be made without the prior written approval of said commissioner.

- 18-29-805.7.2  Written approval.

No permit shall be issued and no construction of such facilities shall be commenced without the prior written approval of the commissioner of sewers and no substantial alteration or addition to or in the sewer or drain or in the preliminary treatment or handling facilities shall be made without the prior written approval of said commissioner.

- Article 9.  Vents

- 18-29-901  General.

- 18-29-901.1  Scope.

The provisions of this article shall govern the materials, design, construction and installation of vent systems.

- 18-29-901.2  Trap seal protection.

The plumbing system shall be provided with a system of vent piping that will permit the admission or emission of air so that the seal of any fixture trap shall not be subjected to a pneumatic pressure differential of more than 1 inch (25 mm) of water (249 Pa).

- 18-29-901.2.1  Venting required.

Every trap and trapped fixture shall be vented in accordance with one of the venting methods specified in this chapter.

- 18-29-901.3  Chemical waste vent system.

The vent system for a chemical waste system shall be independent of the sanitary vent system and shall terminate separately through the roof to the open air.

- 18-29-901.4  Use limitations.

The plumbing vent system shall not be utilized for purposes other than the venting of the plumbing system, except that the waste of a fixture with a value of one fixture unit may be installed to wash out the base of a vent stack.

- 18-29-901.5  Tests.

The vent system shall be tested in accordance with Sections 18-29-312.1 through 18-29-312.2.

- 18-29-901.6  Protection from freezing.

All vent pipes shall be adequately protected from freezing or adequately sized to account for frost build- up.

- 18-29-902  Materials.

- 18-29-902.1  Vents.

The materials and methods utilized for the construction and installation of venting systems shall comply with the applicable provisions of Sections 18-29-702.1 through 18-29-702.6.2.

- 18-29-902.2  Sheet copper.

Sheet copper for vent pipe flashings shall conform to ASTM B 152 and shall weigh not less than 8 ounces per square foot (2.5 kg/m2).

- 18-29-902.3  Sheet lead.

Sheet lead for vent pipe flashings shall weigh not less than 3 pounds per square foot (15 kg/m2) for field- constructed flashings and not less than 2 1/2 pounds per square foot (12 kg/m2) for prefabricated flashings.

- 18-29-902.4.

See Section 18-29-305.7, Water Proofing of Openings.

- 18-29-903  Vent Stacks and Stack Vents.

- 18-29-903.1  Main vent required.

Every sanitary drainage system receiving the discharge of a water closet shall have a main vent that is either a vent stack or a stack vent. Such vent shall run undiminished in size and as directly as possible from the building drain through to the open air above the roof.

- 18-29-903.2  Vent stack required.

A vent stack or a main vent shall be installed with a soil or waste stack whenever continuous vents or other branch vents are required in two or more intervals.

- 18-29-903.3  Vent termination.

Every vent stack or stack vent shall extend outdoors and terminate to the open air.

- 18-29-903.4  Vent connection at base.

Every vent stack shall connect to the base of the drainage stack. The vent stack shall connect at or below the lowest horizontal branch. Where the vent stack connects to the building drain, the connection shall be located within ten pipe diameters downstream of the drainage stack.

- 18-29-903.5  Vent headers.

Stack vents and vent stacks connected into a common vent header at the top of the stacks and extending to the open air at one point shall be sized in accordance with the requirements of Section 18-29-916.1. The number of fixture units shall be the sum of all fixture traits on all stacks connected thereto, and the developed length shall be the longest vent length from the intersection at the base of the most distant stack to the vent terminal in the open air, as a direct extension of one stack.

- 18-29-904  Vent Terminals.

- 18-29-904.1  Roof extension.

All open vent pipes that extend through a roof shall be terminated at least 12 inches (mm)* above the roof; except that where a roof is to be used for any purpose other than weather protection, the vent extensions shall be run at least 7 feet (2134 mm) above the deck or walking surface.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “(305 mm)”.

- 18-29-904.2  Frost closure.

Every vent extension through a roof or wall shall be a minimum of 4 inches (100 mm) in diameter. Any increase in the size of the vent shall be made inside the structure a minimum of 1 foot (305 mm) below the roof or inside the wall.

- 18-29-904.3  Flashings.

The juncture of each vent pipe with the roof line shall be made water tight by an approved flashing.

- 18-29-904.4  Prohibited use.

Vent terminals shall not be used as a flag pole or to support flag poles, TV aerials or similar items.

- 18-29-904.5  Location of vent terminal.

No vent terminal from a drainage system shall be directly beneath a door, window, overhead or other ventilating intake opening of the building, nor shall any such vent terminals be within 12 feet (3.66 m) horizontally of such an opening unless it is at least 2 feet (610 mm) above the top of such opening.

- 18-29-904.6  Extension through the wall.

Vent terminals extending through the wall shall terminate a minimum of 12 feet (3.66 m) from the lot line and 12 feet (3.66 m) above average ground level. Vent terminals shall not terminate under the overhang of a structure with soffit vents. Side wall vent terminals shall be protected to prevent birds or rodents from entering or blocking the vent opening.

- 18-29-905  Vent Connections and Grades.

- 18-29-905.1  Connection.

All individual, branch vents shall connect to a vent stack, stack vent or extend to the open air.

- 18-29-905.2  Grade.

All vent and branch vent pipes shall be so graded and connected as to drain back to the drainage pipe by gravity.

- 18-29-905.3  Vent connection to drainage system.

Every dry vent connecting to a horizontal drain shall connect above the centerline of the horizontal drain pipe.

- 18-29-905.4  Vertical rise of vent.

Every dry vent shall rise vertically to a minimum of 6 inches (150 mm) above the flood level rim of the highest trap or trapped fixture being vented.

- 18-29-905.5  Height above fixtures.

A connection between a vent pipe and a vent stack or stack vent shall be made at least 6 inches (150 mm) above the flood level rim of the highest fixture served by the vent, and 42 inches (1067 mm) minimum above finished floor. Horizontal vent pipes forming branch vents, relief vents or loop vents shall be at least 6 inches (150 mm) above the flood level rim of the highest fixture served and 42 inches (1067 mm) above finished floor.

- 18-29-905.6  Side inlet.

Side inlet closet bends are not permitted.

- 18-29-905.7  Vent for future fixtures.

Where the drainage piping has been roughed-in for future fixtures, a rough-in connection for a vent shall be installed a minimum of one-half the diameter of the drain, but not less than the minimum size indicated in Table 18-29-916.1. The vent rough-in shall connect to the vent system. The connection shall be identified to indicate that the connection is a vent.

- 18-29-906  Fixture Vents.

- 18-29-906.1  Distance of trap from vent.

Each fixture trap shall have a protecting vent located so that the slope and the developed length in the fixture drain from the trap weir to the vent fitting are within the requirements set forth in Table 18-29-906.1.

Table 18-29-906.1
Maximum Distance of Fixture Trap from Vent

Size of Trap (inches); Size of Fixture Drain (inches); Slope (inch per foot); Distance from Trap (feet). 1 1/4; 1 1/2; 1/4; 5. 1 1/2; 1 1/2; 1/4; 5. 1 1/2; 2; 1/4; 5. 2; 2; 1/4; 5. 3; 3; 1/8; 5. 4; 4; 1/8; 5.

- 18-29-906.2  Venting of fixture drains.

The vent for a fixture drain, except where serving a fixture with integral taps, such as water closets, shall connect above the weir of the fixture trap being vented.

- 18-29-906.3  Crown vent.

A vent shall not be installed within two pipe diameters of the trap weir.

- 18-29-907  Individual Vent.

- 18-29-907.1  Individual vent permitted.

Each trap and trapped fixture is permitted to be provided with an individual vent. The individual vent shall connect to the fixture drain of the trap or trapped fixture being vented.

- 18-29-908  Common Vent.

- 18-29-908.1  Individual vent as common vent.

An individual vent is permitted to vent two traps or trapped fixtures as a common vent. The traps or trapped fixtures being common vented shall be located on the same floor level.

- 18-29-908.2  Connection at the same level.

Where the fixture drains being common vented connect at the same level, the vent connection shall be at the interconnection of the fixture drains.

- 18-29-908.3  Connection of different levels.

Connections at different levels shall not be permitted.

- 18-29-909  Deliberately omitted.

- 18-29-910  Deliberately omitted.

- 18-29-911  Deliberately omitted.

- 18-29-912  Combination Drain and Vent System.

- 18-29-912.1  Type of fixtures.

A combination drain and vent system shall not serve fixtures other than floor drains receiving only clear water wastes. Appurtenances receiving large quantities or surges of water shall not be discharged to a combination waste and vent.

- 18-29-912.2  Waste piping and trap.

The waste piping and trap in a combination waste and an end vented (both ends) system shall be a minimum of 4 inch (100 mm) diameter. The waste piping and trap shall be at least two pipe increments larger than the pipe size required and at least two pipe increments larger than any fixture/appurtenance discharge tailpiece.

- 18-29-912.2.1  Branches.

A branch more than 15 feet (4.57 m) in length shall be separately vented. The minimum area of any vent installed in a combination waste and vent system shall be one-half the diameter of the drain pipe served, but not less than the minimum indicated in Table 18-29-916.1.

- 18-29-912.2.2  Sinks, lavatories, and other fixtures.

Sinks, lavatories and other fixtures that are roughed-in above the floor shall not be permitted on a combination waste and vent.

- 18-29-912.2.3  Long mains.

Long mains shall be provided with additional relief vents located at intervals of every 100 feet (30.48 m).

- 18-29-912.2.4  Floor drains.

Floor drains shall be vented at the end of the waste line or individually vented.

- 18-29-912.3  Size.

The minimum size of a combination drain and vent pipe shall be in accordance with Table 18-29-912.3.

Table 18-29-912.3
Size of Combination Drain and Vent Pipe
(for Floor Drains Only)

Diameter Pipe (inches); Maximum Number of Drainage Fixture Units. Connecting to a horizontal branch or stack; Connecting to a building drain or building subdrain. 2; 3; 4. 2 1/2; 6; 26. 3; 12; 31. 4; 20; 50. 5; 160; 250. 6; 360; 575.

For SI: 1 inch = 25.4 mm.

- 18-29-913  Island Fixture Venting.

- 18-29-913.1  Limitation.

Island fixture venting shall not be permitted for fixtures other than sinks and lavatories. Residential kitchen sinks with a dishwasher waste connection, a food waste grinder, or both, in combination with the kitchen sink waste, shall be permitted to be vented in accordance with this section.

- 18-29-913.2  Vent connection.

The island fixture vent shall connect to the fixture drain as required for an individual or common vent. The vent shall rise 6 inches (150 mm) vertically above the flood rim level of the fixture being vented before offsetting horizontally or vertically downward before connecting to the outside vent terminal.

- 18-29-913.3  Vent installation below the fixture flood level rim.

The vent located below the flood level rim of the fixture being vented shall be installed as required for drainage piping in accordance with Article 7, except for sizing. The vent shall be sized in accordance with Section 18-29-916.2. The lowest point of the island fixture vent shall connect full size to the drainage system. The connection shall be to a vertical drain pipe or to the top half of a horizontal drain pipe. Clean-outs shall be provided in the island fixture vent to permit rodding of all vent piping located below the flood level rim of the fixtures. Rodding in both directions shall be permitted through a clean-out.

- 18-29-914  Relief Vents – Stacks of More Than 10 Branch Intervals.

- 18-29-914.1  Where required.

Soil and waste stacks in buildings having more than 10 branch intervals shall be provided with a relief vent at each tenth interval installed, beginning with the top floor.

- 18-29-914.2  Size and connection.

The size of the relief vent shall be equal to the size of the vent stack to which it connects. shall* be vented by venting the upper section of the drainage stack and the lower section of the drainage stack system.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “The relief vent shall....”

- 18-29-915  Vents for Stack Offsets.

- 18-29-915.1  Vent for horizontal offset of drainage stack.

Horizontal offsets of drainage stacks shall be vented where five or more branch intervals are located above the offset.

- 18-29-915.2  Upper section.

The upper section of the drainage stack shall be vented as a separate stack with a vent stack connection installed in accordance with Section 18-29-903.4. The offset shall be considered the base of the stack.

- 18-29-915.3  Lower section.

The lower section of the drainage stack shall be vented by a yoke vent connecting between the offset and the next lower horizontal branch. The yoke vent connection shall be permitted to be a vertical extension of the drainage stack. The size of the yoke vent and connection shall be a minimum of the size required for the vent stack of the drainage stack.

- 18-29-916  Vent Pipe Sizing.

- 18-29-916.1  Size of stack vents and vent stacks.

The minimum required diameter of stack vents and vent stacks shall be determined from the developed length and the total of drainage fixture units connected thereto in accordance with Table 18-29-916.1, but in no case shall the diameter be less than one-half the diameter of the drain served or less than 1 1/2 inches (40 mm).

Table 18-29-916.1
Size and Developed Length of Stack Vents and Vent Stacks

Total Fixture Units Being Vented (DFU); Diameter of Vent (inches). 1 1/2**; 2; 2 1/2; 3; 4; 5; 6; 8; 10. Maximum Developed Length of Vent (feet). 8; 100; *. 20; 50; 150; *. 42; 30; 100; 300; *. 60; N.P.; 50; 80; 400; *. 500; N.P.; N.P.; 70; 180; 700; *. 1100; N.P.; N.P.; N.P.; 50; 200; 700; *. 1900; N.P.; N.P.; N.P.; N.P.; 70; 200; 700; *. 3600; N.P.; N.P.; N.P.; N.P.; N.P.; 60; 250; 800; *. 5600; N.P.; N.P.; N.P.; N.P.; N.P.; N.P.; 60; 250; *. 8400; N.P.; N.P.; N.P.; N.P.; N.P.; N.P.; N.P.; N.P.; 0.

*      = Unlimited.

**     = Not permitted for water closets

N.P.     = Not Permitted

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-916.2  Other vents.

The diameter of individual vents, branch vents and relief vents shall be at least one-half the required diameter of the drain served. The required size of the drain shall be determined in accordance with Article 7. Vent pipes shall not be less than 1 1/2 inches (40 mm) in diameter. Vents exceeding 40 feet (12.19 m) in developed length shall be increased by one nominal pipe size for the entire developed length of the vent pipe. Relief vents for soil and waste stacks in buildings having more than 10 branch intervals shall be sized in accordance with Section 18-29-914.2.

- 18-29-916.3  Required sizes of vents.

The length of the vent stack or main vent shall be its developed length from the lowest connection of the vent system with the soil stack, waste stack, or house drain to the vent stack terminal, if it terminates separately in the open air, or to the connection of the vent stack with the stack-vent, plus the developed length of the stack-vent from the connection to the terminal in the open air, if the two vents are connected together with a single extension to the open air. The diameter of an individual vent shall be not less than 1 1/2 inches (40 mm) nor less than one-half the diameter of the drain to which it is connected. The diameter of a relief vent shall be not less than one-half times the diameter of the soil or waste branch to which it is connected. The nominal size of vent piping shall be determined from its length and the total of fixture units connected thereto, as provided in accordance with Table 18-29-916.1 in this section. Twenty percent (20%) of the total length may be installed in a horizontal position.

- 18-29-916.4  Multiple branch vents.

Where multiple branch vents are connected to a common branch vent, the common branch vent shall be sized in accordance with this section based on the size of the common horizontal drainage branch that is or would be required to serve the total drainage fixture unit (dfu) load being vented.

- 18-29-916.4.1  Multiple branch vents exceeding 40 feet.

Multiple branch vents exceeding 40 feet (12.19 mm) in developed length shall be increased by nominal size for the entire developed length of the vent pipe.

- 18-29-916.5  Sump vents.

Sump vent sizes shall be determined in accordance with Section 18-29-916.5.1.

- 18-29-916.5.1  Sewage pumps and sewage ejectors other than pneumatic.

Drainage piping below sewer level shall be vented in a similar manner to that of a gravity system. Building sump vent sizes for sumps with sewage pumps or sewage ejectors, other than pneumatic, shall be determined in accordance with Table 18-29-916.5.1.

Table 18-29-916.5.1
Size and Length of Sump Vents

Discharge Capacity of Pump (gpm); Maximum Developed Length of Vent (feet) a. Diameter of vent (inches). 1 1/4; 1 1/2; 2; 2 1/2; 3; 4. 10; No limit b; No limit; No limit; No limit; No limit; No limit. 20; 270; No limit; No limit; No limit; No limit; No limit. 40; 72; 160; No limit; No limit; No limit; No limit. 60; 31; 75; 270; No limit; No limit; No limit. 80; 16; 41; 150; 380; No limit; No limit. 100; 10c; 25; 97; 250; No limit; No limit. 150; N.P.; 10 c; 44; 110; 370; No limit. 200; N.P.; N.P.; 20; 60; 210; No limit. 250; N.P.; N.P.; 10; 36; 132; No limit. 300; N.P.; N.P.; 10 c; 22; 88; 380. 400; N.P.; N.P.; N.P.; 10 c; 44; 210. 500; N.P.; N.P.; N.P.; N.P.; 24; 130.

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 gpm = 3.785 L/m.

a Developed length plus an appropriate allowance for entrance losses and friction due to fittings, changes in direction and diameter. Suggested allowances shall be obtained from NBS Monograph 31 or other approved sources. An allowance of 50 percent of the developed length shall be assumed if a more precise value is not available.

b Actual values greater than 500 feet.

c Less than 10 feet.

- 18-29-916.5.2  Pneumatic sewage ejectors.

The air pressure relief pipe from a pneumatic sewage ejector shall be connected to an independent vent stack terminating as required for vent extensions through the roof. The relief pipe shall be sized to relieve air pressure inside the ejector to atmospheric pressure, but shall not be less than 3 inches (75 mm).

- 18-29-917  Vents Not Required.

- 18-29-917.1  Not required.

No vent will be required on a downspout trap, a subsoil catch basin trap draining by gravity to the house drain or sewer, or a basement floor drain which branches into the house drain at a distance of more than 5 feet from any soil or waste stack. Other floor drains below grade shall be vented at the end of the waste line or individually vented.

- 18-29-918  Deliberately omitted.

- Article 10.  Traps, Separators and Interceptors

- 18-29-1001  General.

- 18-29-1001.1  Scope.

This article shall govern the material and installation of traps, interceptors and separators.

- 18-29-1002  Trap Requirements.

- 18-29-1002.1  Fixture traps.

Each plumbing fixture shall be separately trapped by a water-seal trap, except as otherwise permitted by this chapter. The trap shall be placed as close as possible to the fixture outlet. The vertical distance from the fixture outlet to the trap weir shall not exceed 24 inches (610 mm). The distance of a clothes washer standpipe above a trap shall conform to Section 18-29-802.4. A fixture shall not be double trapped. An automatic clothes washer or laundry tub shall not discharge to a trap service or a kitchen sink.

Exceptions:

1.     Sections 18-29-1002.1.1 through 18-29-1002.10 shall not apply to fixtures with integral traps.

2.     A combination plumbing fixture is permitted to be installed on one trap provided that one compartment is not more than 6 inches (150 mm) deeper than the other compartment and the waste outlets are not more than 30 inches (762 mm) apart.

3.     A grease trap intended to serve as a fixture trap in accordance with the manufacturer's installation instruction shall be permitted to serve as the trap for a single fixture or a combination sink of not more than three compartments where the vertical distance from the fixture outlet to the inlet of the interceptor does not exceed 30 inches (762mm), and the developed length of the waste pipe from the most upstream fixture outlet to the inlet of the interceptor does not exceed 5 feet (1525 mm). When the developed length exceeds 5 feet (1525 mm), or more than one fixture or receptacle is connected to an interceptor, each shall be individually trapped and vented. All receptors shall be individually trapped and vented. Wastes exceeding 140°F shall be cooled before draining into any grease interceptor or interceptor or catch basin.

- 18-29-1002.1.1  Open plumbing.

All sinks, lavatories, and laundry trays shall be so installed as to provide for access to traps and waste connections.

- 18-29-1002.1.2  Traps underground.

Underground traps shall be provided with accessible and removable clean-outs, except for separate “P” traps into which floor drains, urinals and other fixtures with removable drain strainers discharge.

- 18-29-1002.1.3  Animal facilities and barn drainage.

All wastes from barns, stables, animal facilities or yards for animals shall be intercepted before entering the sewer by an interceptor or catch-basin, which shall be trapped and covered with a tight iron cover, and such catch-basins, if within buildings, shall be provided with a vent not less than 3 inches (75 mm) in diameter carried through the roof. All floor drains and wash racks shall be provided with deep seal traps and heavy strainers.

- 18-29-1002.1.4  Basement floor drains.

Basement floor drains shall connect into a trap so located and constructed that it can be readily cleaned and of a size to serve the purpose for which it is intended but in no case less than 3 inches. The drain inlet shall be accessibly located.

- 18-29-1002.1.5  Backwater valves.

See Section 18-29-715, Backwater Valves.

- 18-29-1002.2  Design of traps.

Fixture traps shall be self-scouring. Fixture traps shall not have interior partitions, except where such traps are integral with the fixture or where such traps are constructed of an approved material that is resistant to corrosion and degradation. Slip joints shall be made with an approved elastomeric gasket and shall only be installed on the trap inlet, trap outlet and within the trap seal.

- 18-29-1002.3  Prohibited traps.

The following types of traps are prohibited:

1.     Traps that depend on moving parts to maintain the seal;

2.     Bell traps;

3.     Crown-vent traps;

4.     Separate fixture traps that depend on interior partitions for the seal, except those traps constructed of an approved material that is resistant to corrosion and degradation;

5.     “S” traps;

6.     Drum traps;

7.     Building (house) traps in sanitary sewers.

- 18-29-1002.4  Trap seals.

Each fixture shall have a liquid seal of not less than 2 inches (50 mm) and not more than 4 inches (100 mm), or deeper for special designs relating to accessible fixtures. Where a trap seal is subject to loss by evaporation, a deep-seal trap consisting of a 4-inch (100 mm) seal is required, or other means shall be provided to prevent loss of trap seal. Other means shall include: automatic trap seal primers conforming to ASSE 1018 or ASSE 1044, or vegetable or mineral oil added to the trap.

- 18-29-1002.5  Size of fixture traps.

Fixture trap size shall be not less than the size indicated in Table 18-29-709.1. A trap shall not be larger than the drainage pipe into which the trap discharges.

- 18-29-1002.6  Deliberately omitted.

- 18-29-1002.7  Trap setting and protection.

Traps shall be set level with respect to the trap seal and, where necessary, shall be protected from freezing.

- 18-29-1002.8  Recess for trap connection.

A recess provided for connection of the underground trap, such as one serving a bathtub in slab-type construction, shall have sides and a bottom of corrosion-resistant, insect-and vermin-proof construction.

- 18-29-1002.9  Acid-resisting traps.

Where a vitrified clay or other brittleware, acid-resisting trap is installed underground, such trap shall be embedded in concrete extending 6 inches (152 mm) beyond the bottom and sides of the trap.

- 18-29-1002.10  Plumbing in mental health centers.

In mental health centers, pipes and traps shall not be exposed.

- 18-29-1003  Interceptors and Separators.

- 18-29-1003.1  Interceptors required.

Interceptors for oil, grease, sand and other substances harmful or hazardous to the building drainage system, the public sewer or sewage treatment plant, or processes shall be provided as required in this chapter. The use of interceptors shall be determined by the department of sewers and as referenced in the current edition of the permit requirement and fees book.

- 18-29-1003.1.1  Interceptors not required.

An interceptor shall not be required for single family dwellings, multiple residential dwelling buildings with six dwelling units or less and pantry sinks in office building break rooms where no oven, stove or range is in use.

- 18-29-1003.2  Size, type and location to be approved.

The size, type and location of each interceptor and of each separator shall be designed and installed in accordance with the manufacturer's instructions, the department of sewers standards and as referenced in the current edition of the permit requirements and fees book, and the requirements of this section based on the anticipated conditions of use. Wastes that do not require treatment or separation need not be discharged into any interceptor or separator. All interceptors shall be installed in an accessible location to permit the convenient removal of the lid and internal contents.

- 18-29-1003.3  Grease interceptor or catch basin.

A grease interceptor or catch basin shall be provided where indicated in Sections 18-29-1003.3.1 through 18-29-1003.3.8.

- 18-29-1003.3.1  Where required.

Every multiple dwelling building with over six dwelling units (exclusive of townhouses), any commercial kitchen, and where required by the department of sewers, shall be provided with a grease interceptor or an outside catch basin for all kitchen wastes.

- 18-29-1003.3.2  Grease, fats and oils.

Sinks or other fixtures in restaurants, hotels, clubhouses, public institutions, butcher shops, plumbing systems for institutions or commercial establishments in which grease, fats, culinary oils, or similar waste products from kitchens or food processing areas are wasted in connection with utensil, vat, dish or floor cleaning processes, shall include grease interceptors. All waste lines and drains carrying grease, fats, or culinary oil, in the above establishments shall be directed to one or more interceptors, located as close as practical to the fixtures served, or to an inside or outside catch basin.

- 18-29-1003.3.3  Construction materials.

All grease interceptors and catch basins located within buildings shall be constructed of precast concrete, concrete with the bottom, sides and baffles poured monolithically, heavy cast-iron or equally durable metal and shall be vented as provided with a gas tight metal cover, securely fastened. All grease interceptors and catch basins shall have a capacity to intercept and retain not less than 90 percent of the grease received.

- 18-29-1003.3.4  Grease interceptors and discharge.

No grease interceptor shall receive the discharge from a food waste disposal or a commercial dishwashing machine.

- 18-29-1003.3.5  Types.

Type of interceptor required for commercial kitchens and multiple residential dwelling units exceeding six dwelling units shall be determined by the department of sewers.

- 18-29-1003.3.6  Grease trap capacity.

Grease traps shall have the grease retention capacity indicated in Table 18-29-1003.3.6 for the flow- through rates indicated.

Table 18-29-1003.3.6
Capacity of Grease Traps

Total Flow-Through Rating (gpm); Grease Retention Capacity (pounds). 4; 8. 6; 12. 7; 14. 9; 18. 10; 20. 12; 24. 14; 28. 15; 30. 18; 36. 20; 40. 25; 50. 35; 70. 50; 100.

For SI: 1 gpm = 3.785 L/m, 1 pound = 0.454 kg.

- 18-29-1003.3.7  Rate of flow controls.

Inside grease traps shall be equipped with devices to control the rate of water flow so that the water flow does not exceed the rated flow. The flow-control device shall be vented and terminate not less than 6 inches (150 mm) above the flood rim level or installed in accordance with the manufacturer's instructions.

- 18-29-1003.3.8  Efficiency of interceptors.

Interceptors shall conform to PDI G 101 and shall be installed in accordance with the manufacturer's instructions.

- 18-29-1003.4  Grease catch basins outside.

A grease catch basin located outside a building shall be of concrete, precast in blocks or monolithic or a brick construction with the block or brick laid up in portland cement mortar with walls not less than 5 inches (125 mm) thick, and bottom not less than 2 inches (50 mm) thick. The basin shall be watertight. The basin shall be not less than 36 inches (914 mm) in diameter below the top of the highest inlet pipe. The bottom of the basin shall be not less than 36 inches (914 mm) below the invert of the outlet pipe. The outlet pipe shall be trapped with a catch basin trap and of material as required by this chapter. The catch basin trap shall have a minimum seal of 4 inches (100 mm) and shall have an accessible cleanout of a minimum of 3 inches (75 mm).

- 18-29-1003.4.1  Basin cover.

The basin shall be covered with an all cast-iron cover or cast-iron lid in a stone or concrete ring and with a minimum opening of 16 inches (406 mm). The lid shall not be less than 1/4 inch (6 mm) thick.

- 18-29-1003.5  Deliberately omitted.

- 18-29-1003.6  Volatile waste separator.

Gasoline, benzine, naphtha, and other volatile, flammable or explosive wastes shall not discharge into a house sewer, public sewer, or sewage treatment plant. Such wastes shall be intercepted in approved triple basins having a liquid retention of not less than 2 cubic feet each, (0.19 m3) and the volatile, flammable or explosive constituents removed. Every system of basins within buildings shall be constructed of extra heavy cast iron or equally durable material. A heavy iron cover shall be securely bolted into place and made gas-tight with a soft metallic gasket. The outlet from such basins and the inlet of the first basin shall be trapped with a seal of not less than 4 inches (100 mm). The inlet trap of the first basin shall be omitted when floor drains are individually trapped. A vent pipe of not less than 2 inches (50 mm) in diameter shall be connected to the basins, not less than 4 inches above the top of the outlet and extended independently to the outer air.

- 18-29-1003.6.1  Garages.

In areas of garages where motor fuels are dispensed or where motor vehicles are serviced, each floor drain shall be properly trapped. In other garage areas or parking facilities, floor drains need not be trapped. Floor drains above the level of the basins shall connect to a stack extending independently to the outer air and the vents of the basins shall be connected 6 inches (152 mm) or higher than the lowest floor drain.

- 18-29-1003.7  Separation of liquids.

A mixture of treated or untreated light and heavy liquids with various specific gravities shall be separated in approved receptacle. Separators shall be designed in accordance with Sections 18-29-1003.7.1 and 18-29-1003.7.2.

- 18-29-1003.7.1  General design requirements.

Oil separators shall have a depth of not less than 2 feet (610 mm) below the invert of the discharge drain. The outlet opening of the separator shall not have less than 18-inch (457 mm) water seal.

- 18-29-1003.7.2  Garage and service stations.

Where automobiles are serviced, greased, repaired or washed or where gasoline is dispensed, separators shall have a minimum capacity of 6 cubic feet (0.17 m3) for the first 100 square feet (9.3 m2) of area to be drained into the separator. Parking garages in which servicing, repairing or washing is not conducted, and in which gasoline is not dispensed, shall require a triple basin. Areas of commercial garages utilized only for storage of automobiles are required to be drained through a triple basin.

- 18-29-1003.8  Sand interceptors in commercial establishments.

Sand and similar interceptors for heavy solids shall be designed and located so as to be provided with ready access for cleaning, and shall have a water seal of not less than 6 inches (150 mm).

- 18-29-1003.9  Laundries.

Commercial laundries shall be equipped with an interceptor with a wire basket or similar device, removable for cleaning, that prevents passage into the drainage system of solids 1/2 inch (12 mm) or larger in size, string, rags, buttons, or other materials detrimental to the public sewage system.

- 18-29-1003.10  Bottling establishments.

Bottling plants shall discharge process wastes into an interceptor that will provide for the separation of broken glass or other solids before discharging waste into the drainage system.

- 18-29-1003.11  Slaughterhouses.

Slaughtering room and dressing room drains shall be equipped with approved separators. The separator shall prevent the discharge into the drainage system of feathers, entrails and other materials that cause clogging.

- 18-29-1003.12  Venting of interceptors and separators.

Interceptors and separators shall be designed so as not to become air bound where tight covers are utilized. Each interceptor or separator shall be vented where subject to a loss of trap seal.

- 18-29-1003.13  Access and maintenance of interceptors and separators.

Access shall be provided to each interceptor and separator for service and maintenance. Interceptors and separators shall be maintained by periodic removal of accumulated grease, scum, oil, or other floating substances and solids deposited in the interceptors or separators.

- 18-29-1004  Materials, Joints and Connections.

- 18-29-1004.1  General.

The materials and methods utilized for the construction and installation of traps, interceptors and separators shall comply with this chapter and the applicable provisions of Article 7. The fittings shall not have ledges, shoulders or reductions capable of retarding or obstructing flow of the piping.

- Article 11.  Storm Drainage

- 18-29-1101  General.

- 18-29-1101.1  Scope.

The provisions of this article shall govern the materials, design, construction and installation of storm drainage.

- 18-29-1101.2  Where required.

Storm drainage shall be provided pursuant to Sections 18-29-1101.2.1 through 18-29-1102.3.

- 18-29-1101.2.1  Roof drainage and downspouts.

All roofs exceeding 750 square feet (69.7 m2) in area shall be drained to a sewer, where such is available in any adjoining public way, or public place. Every connecting roof downspout having the open roof connection, located nearer than 12 feet (3.66 m) to an inside lot line or any door or window on the same premises, shall be trapped on the downspout side of the connection to any sanitary sewer or any combined sewer or drain, and shall be set where not subject to frost.

Exceptions:

1.     Nothing in this provision shall prohibit the temporary or permanent disconnection of the roof downspout of a building from the sewer or combined sewer so long as the disconnection does not result in the drainage of water beyond the property lines of the lot on which the building is located.

2.     Roofs of single-family (Class A-1) and multiple-family (Class A-2) buildings may be provided with external downspouts discharging onto a paved or landscaped area, provided the water thus discharged can be drained directly to an area drain, catch basin or street gutter connected to a public sewer, without spilling over onto adjacent property creating a public hazard or nuisance.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-1101.2.2  Drainage of areas and yards.

Outside areas other than roof areas may be drained to a sewer and when paved shall be so drained where necessary to avoid the discharge of water onto adjoining premises. Paved areas of 400 square feet or less where connected to the sewer shall be provided with trapped connections before connecting to any sanitary sewer or combined sewer, with traps placed where not subject to frost. Outside areas exceeding 400 square feet (37.2 m2), and not more than 5,000 square feet (1,524 m2), where connected to sewers, shall be connected through a catchbasin, not less than 3 feet (915 mm) in diameter and not less than 3 feet (915 mm) deep below the bottom of the trap. Areas of more than 5,000 square feet (1,524 m2) shall be provided with a catchbasin not less than 4 feet (1,220 mm) in diameter and not less than 3 feet 6 inches (1,067 mm) deep below the bottom of the trap.

- 18-29-1101.2.3  Storm runoff.

Construction which is tributary to the combined sewer system of the city of Chicago shall be designed to minimize and/or delay runoff inflow contributions to the combined sewer system in accordance with the following:

1.     Disconnection. For sites of 5,000 square feet (1,524 m2) in area and smaller, except multiple unit developments, storm runoff will be minimized or delayed by the disconnection of downspouts, temporary or otherwise, in accordance with Section 18-29-1101.2.1 and any other applicable sections of this chapter and the department of sewers design standards.

2.     Detention. For sites greater than 5,000 square feet (1,524 m2), and multiple unit developments, storm runoff shall be detained in accordance with, and is required by, the department of sewers design standards. The release rate of detained storm runoff shall be managed on the available capacity of the combined storm sewer system as determined by the department of sewers.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-1101.3  Prohibited drainage.

Storm water shall not be drained into sewers intended for sewage only.

- 18-29-1101.4  Tests.

The conductors and the building storm drain shall be tested in accordance with Sections 18-29-312.1 through 18-29-312.9.

- 18-29-1101.5  Continuous flow.

The size of a drainage pipe shall not be reduced in the direction flow.*

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “...direction of the flow.”

- 18-29-1101.6  Fittings and connections.

All connections and changes in direction of the storm drainage system shall be made with approved drainage-type fittings in accordance with Table 18-29-706.3. The fittings shall not obstruct or retard flow in the system.

- 18-29-1101.7  Roof design.

The structural integrity of roofs shall be designed for the maximum possible depth of water that will pond thereon as determined by the relative levels of roof deck and overflow weirs, scuppers, edges or serviceable drains in combination with the deflected structural elements.

- 18-29-1101.8  Cleanouts required.

Cleanouts shall be installed in the storm drainage system and shall comply with the provisions of this chapter for sanitary drainage pipe cleanouts or as required by the department of sewers design standards.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-1101.9  Backwater valves.

Backwater valves installed in a storm drainage system shall conform to Section 18-29-715.

- 18-29-1102  Materials.

- 18-29-1102.1  General.

The materials and methods utilized for the construction and installation of storm drainage systems shall comply with this section and the applicable provisions of Article 18-29-7.

- 18-29-1102.2  Inside storm drainage conductors.

Inside storm drainage conductors installed above ground shall conform to one of the standards listed in Table 18-29-702.1.

- 18-29-1102.3  Underground building storm drain pipe.

Underground building storm drain pipe shall conform to one of the standards listed in Table 18-29-702.2, except that neither polyvinyl chloride (PVC) nor polypropylene (PPL) pipe and fittings shall be allowed in stormwater detention applications as oversized pipe.

- 18-29-1102.4  Building storm sewer pipe.

Building storm sewer pipe shall conform to one of the standards listed in Table 18-29-702.3, except that neither polyvinyl chloride (PVC) nor polypropylene (PPL) pipe and fittings shall be allowed in stormwater detention applications as oversized pipe.

(Amend Coun. J. 3-27-02, p. 82090, §§ 1, 3)

- 18-29-1102.5  Subsoil drain pipe.

Subsoil drains shall be open-jointed, horizontally split or perforated pipe conforming to one of the standards listed in Table 18-29-1102.5.

Table 18-29-1102.5
Subsoil Drain Pipe

Material; Standard. Cast-iron pipe; ASTM A 74; ASTM A 888; CISPI 301. Polyvinyl chloride (PVC) plastic pipe (Type Sewer Pipe, PS25, PS50 or PS100); ASTM D 2729; ASTM D 3034; ASTM F891; CAS-B182.2; CSA CAN/CSA-B182.4; SDR 35. Vitrified clay pipe; ASTM C 4; ASTM C 700.

- 18-29-1102.6  Roof drains.

Roof drains shall conform to ASME A112.21.2.

- 18-29-1102.7  Fittings.

Pipe fittings shall be approved for installation with the piping material installed, and shall conform to the respective pipe standards or one of the standards listed in Table 18-29-702.4. The fittings shall not have ledges, shoulders or reductions capable of retarding or obstructing flow in the piping. Threaded drainage pipe fittings shall be of the recessed drainage type.

- 18-29-1103  Traps.

- 18-29-1103.1  Main trap.

Leaders and storm drains connected to a combined sewer shall be trapped. Individual storm water traps shall be installed on the storm water drain branch serving each conductor, or a single trap shall be installed in the main storm drain just before its connection with the combined building sewer or the public sewer. One trap may serve more than one downspout, and any such trap shall be on the downstream side of the connection to any sanitary sewer or any combined sewer or drain, and shall be set where not subject to frost.

- 18-29-1103.2  Material.

Storm water traps, when required, shall be of the same material as the piping system to which they are attached.

- 18-29-1103.3  Size.

Traps for individual conductors shall be the same size as the horizontal drain to which they are connected.

- 18-29-1103.4  Cleanout.

An accessible cleanout shall be installed on the building side of the trap.

- 18-29-1104  Conductors and Connections.

- 18-29-1104.1  Prohibited use.

Conductor pipes shall not be used as soil, waste or vent pipes, and soil, waste or vent pipes shall not be used as conductors.

- 18-29-1104.1.1  District sewer lines.

In service areas developed after May 30, 2003, where separate sanitary and storm sewers are constructed, drain connections for buildings constructed after May 30, 2003 shall have separate sanitary waste water and storm water connections.

(Added Coun. J. 5-7-03, p. 621, § 1)

- 18-29-1104.2  Combining storm with sanitary drainage.

The sanitary and storm drainage systems of a structure shall be entirely separate except where combined sewer systems are utilized. Where a combined sewer is utilized, the building storm drain shall be connected in the same horizontal plane at or downstream of where the building drain exits the building.

- 18-29-1104.2.1  Separate sewer systems.

Where feasible, storm water inflows to the existing combined sewer in the public right-of-way shall be directed to a separate storm sewer, should a separate public storm sewer become available. Such re-direction of storm water inflows shall take place within five years of the establishment and availability of a separate public storm sewer, or such reasonable longer period of time as in the judgment of the commissioner of water management is necessary to accomplish such re- direction. This requirement shall not apply to buildings in existence on May 30, 2003, located on private property, that do not have distinct sanitary waste water and storm water connections.

(Added Coun. J. 5-7-03, p. 621, § 1)

- 18-29-1104.3  Floor drains.

Floor drains shall not be connected to a storm drain.

- 18-29-1105  Roof Drains.

- 18-29-1105.1  Strainers.

Roof drains shall have strainers extending not less than 4 inches (100 mm) above the surface of the roof immediately adjacent to the roof drain. Strainers shall have an available inlet area, above roof level, of not less than one and one-half times the area of the conduct or leader to which the drain is connected. All downspouts from gravel roofs shall be fitted with serviceable devices to screen out loose gravel.

- 18-29-1105.2  Flat decks.

Roof drain strainers for use on recreational decks, sun decks, parking decks and similar areas that are normally serviced and maintained shall comply with Section 18-29-1105.1 or shall be of the flat-surface type, installed level with the deck, with an available inlet area not less than two times the area of the conductor or leader to which the drain is connected.

- 18-29-1105.3  Roof drain flashing.

The connection between roofs and roof drains which pass through the roof and into the interior of the building shall be made water tight by the use of approved flashing material. Refer to Section 18-29-305.7.

- 18-29-1105.4  Maximum area.

A single roof drain head shall not exceed 13,000 square feet (1,208 m2).

- 18-29-1106  Size of Conductors, Leaders and Storm Drains.

- 18-29-1106.1  General.

The size of the vertical conductors and leaders, building storm drains, building storm sewers, and any horizontal branches of such drains or sewers shall be in compliance with Sections 18-29-1106.2 through 18-29-1106.6.

- 18-29-1106.2  Vertical conductors and leaders.

No downspout shall be of smaller size than shown in Table 18-29-1106.2, based on the maximum horizontal projected roof area drained. Downspouts that are offset at 90 degrees shall be sized as a horizontal storm drain and shall be full size to the storm drain or sewer or combined drain or sewer. The above sizes of downspouts are based on the diameter of circular downspouts and other shapes shall have equivalent cross-sectional area.

Table 18-29-1106.2
Downspouts

Diameter of Downspout (inches); Max. Horizontal Projected Roof Area (square feet). 2; 720. 2 1/2; 1,300. 3; 2,150. 4; 4,600. 5; 8,300. 6; 13,000. 8; 29,000. 10; 52,000. 12; 83,000. 13; 155,000.

- 18-29-1106.3  Building storm drains and sewers.

The size of the building storm drain, building storm sewer and their horizontal branches shall be based on the maximum projected roof area in accordance with Table 18-29-1106.3. The minimum slope of horizontal branches shall be one-eighth unit vertical in 12 units horizontal (1-percent slope) unless otherwise approved.

- 18-29-1106.4  Vertical walls.

In sizing roof drains and storm drainage piping, 25 percent of the area of any vertical wall that diverts rainwater to the roof shall be added to the projected roof area for inclusion in calculating the required size of vertical conductors, leaders and horizontal storm drainage piping.

- 18-29-1106.5  Parapet wall scupper location.

Parapet wall roof drainage scupper location shall comply with the requirements of Section 18-29-1101.7.

Exception: Scuppers are not permitted in fire walls and lot-line parapets, provided in accordance with Chapter 15-8.

- 18-29-1106.6  Size of roof gutters.

The size of semicircular gutters shall be based on the maximum projected roof area in accordance with Table 18-29-1106.6.

Table 18-29-1106.3
Size of Horizontal Storm Drainage Piping

For a printer-friendly PDF version of Table 18-29-1106.3, please click here.

1/8 Unit Vertical in 12 Units Horizontal (1-percent slope); 1/4 Unit Vertical in 12 Units Horizontal (2-percent slope); 1/2 Unit Vertical in 12 Units Horizontal (4-percent slope). Pipe Size; Square Feet; Square Feet; Square Feet. 3; 822; 1,160; 1,644. 4; 1,800; 2,650; 3,760. 5; 3,340; 4,720; 6,680. 6; 5,350; 7,550; 10,700. 8; 11,500; 16,300; 23,000. 10; 20,700; 29,200; 41,400. 12; 33,300; 47,000; 66,600. 15; 599,500; 84,000; 119,000.

For SI: 1 inch = 25.4 mm, 1 square foot = 0.0929*

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “0.0929 m2 ”.

Table 18-29-1106.6
Size of Semicircular Roof Gutters

Diameter of Gutters (inches); Square Feet; Diameter of Gutters (inches); Square Feet; Diameter of Gutters (inches); Square Feet; Diameter of Gutters (inches); Square Feet. 1/16 Unit Vertical in 12 Units Horizontal (0.5-percent slope); 1/8 Unit Vertical in 12 Units Horizontal (1-percent slope); 1/4 Unit Vertical in 12 Units Horizontal (2-percent slope); 1/2 Unit Vertical in 12 Units Horizontal (4-percent slope). 3; 170; 3; 240; 3; 340; 3; 480. 4; 360; 4; 510; 4; 720; 4; 1,020. 5; 625; 5; 880; 5; 1,250; 5; 1,770. 6; 960; 6; 1,360; 6; 1,920; 6; 2,770. 7; 1,380; 7; 1,950; 7; 2,760; 7; 3,900. 8; 1,990; 8; 2,800; 8; 3,980; 8; 5,600. 10; 3,600; 10; 5,100; 10; 7,200; 10; 10,000.

For SI: 1 inch = 25.4 mm, 1 square foot = 0.929 m2

- 18-29-1107  Deliberately omitted.

- 18-29-1108  Combined Sanitary and Storm System.

- 18-29-1108.1  Size of combined drains and sewers.

Whenever a combined sewer system is employed, the required size of the combined house sewer shall be determined by adding the total drained area in square feet in Table 18-29-1106.2 and equivalent area for the number of fixture units in accordance with Table 18-29-1108.1.

Table 18-29-1108.1
Combined Sanitary and Storm System

No. of Fixture Units; Equivalent Area (sq. ft.); No. of Fixture Units; Equivalent Area (sq. ft.)*. 1; 165; 31; 2,820. 2; 325; 32; 2,870. 3; 475; 34; 2,955. 5; 750; 38; 3,125. 6; 875; 40; 3,200. 7; 1,000; 42; 3,270. 8; 1,115; 44; 3,340. 9; 1,225; 46; 3,400. 10; 1,330; 48; 3,465. 11; 1,435; 50; 3,350. 12; 1,530; 55; 3,530. 13; 1,620; 60; 3,790. 14; 1,710; 65; 3,900. 15; 1,800; 70; 4,000. 16; 1,880; 75; 4,090. 17; 1,960; 80; 4,175. 18; 2,040; 85; 4,250. 19; 2,110; 90; 4,320. 20; 2,180; 95; 4,390. 21; 2,250; 100; 4,450. 22; 2,310; 105; 4,500. 23; 2,360; 110; 4,550. 24; 2,440; 115; 4,600. 25; 2,500; 120; 4,645. 26; 2,550; 125; 4,690. 27; 2,600; 130; 4,725. 28; 2,660; 140; 4,800. 29; 2,710; 145; 4,830. 30; 2,770; 150; 4,850.

* For more than 150 fixture units, the equivalent area shall be determined by adding 7.2 square feet for each fixture unit over 150 to 4,850 square feet.

- 18-29-1109  Values for Continuous Flow.

- 18-29-1109.1  Equivalent roof area.

Where there is a continuous or semi-continuous discharge into the building storm drain or building storm sewer, such as from a pump, ejector, air conditioning plant or similar device, each gallon per minute (L/m) of such discharge shall be computed as being equivalent to 24 square feet (2.25 m2) of roof area. (See Table 18-29-1108.1)

- 18-29-1110  Controlled Flow Roof Drain Systems.

- 18-29-1110.1  General.

The roof of a structure shall be designed for the storage of water where the storm drainage system is engineered for controlled flow. The controlled flow roof drain system shall be an engineered system in accordance with this section and the design, submittal, approval, inspection and testing requirements of Section 18-29-1105.4. In lieu of the conventional downspout requirements of Section 18-29-1106, controlled flow roof drainage may be used. The water of a 25 year frequency shall not be stored on the roof for more than 24 hours. The water depth on flat roofs shall not exceed 3 inches (75 mm) during the above storm and 3 inches (75 mm) average depth on sloped roofs not exceeding 6 inches (32 mm) rise or depth of slope.

- 18-29-1110.1.1  Design.

The flow rate (gpm) shall be determined by the use of Chart 18-29-1110.1.1 A for flat roofs and Chart 18-29-1110.1.1 B for slope roofs. The size of the vertical pipe and horizontal pipe shall be determined by the use of Tables 18-29-1110.1.1 C for vertical pipe and Table 18-29-1110.1.1 D for horizontal pipe and in no case shall be less than 3 inches (75 mm). The capacity rating (gpm) of any controlled flow downspout, branch or storm drain shall be converted to an equivalent square foot area by multiplying the gallons per minute (gpm) by 24 (24 square feet of roof area equals 1 gpm) before connecting to any combined house drain or house sewer, and add this value to the total drained area of Section 18-29-1106 of this chapter. Downspouts that are offset at 90 degrees shall be full size to the storm drain or sewer or combined drain or sewer.

Chart 18-29-1110.1.1 A and
Chart 18-29-1110.1.1 B

Table 18-29-1110.1.1

Diameter of Downspout; Max. Horizontal Projected Roof Area Square Feet. 2"; 720. 2 1/2"; 1,300. 3"; 2,150. 4"; 4,600. 5"; 8,300. 6"; 13,000. 8"; 29,000. 10"; 52,000. 12"; 83,000. 13"; 155,000.

Table 18-29-1110.1.1C
Vertical

Diameter of Downspout; Max. Vertical Projected Roof Area Square Feet. 3"; 88. 4"; 190. 5"; 345. 6"; 560. 8"; 1210. 10"; 2185. 12"; 3570. 15"; 6450.

Table 18-29-1110.1.1D
Horizontal

Maximum Controlled Flow in GPM. Pipe Diameter in Inches; Slope in Inches in gpm. 1/2; 1/4; 1/8; 1/16. 3"; 72; 51; N.P.; N.P.. 4"; 156; 110; 78; N.P.. 5"; 282; 200; 140; N.P.. 6"; 460; 325; 230; N.P.. 8"; 990; 700; 495; N.P.. 10"; 1,795; 1,265; 895; 630. 12"; 2,065; 1,460; 1,030. 15"; 2,650; 1,870.

- 18-29-1110.2  Control devices.

The control devices shall be installed so that the rate of discharge of water per minute shall not exceed the values for continuous flow as indicated in Section 18-29-1110.1.1. A scupper drain or drains shall be placed in the parapet wall at an invert elevation 1/2 inch (12 mm) above the maximum designed head. The scupper shall have a cross sectional area equal to that as required for conventional roof drainage. Control of runoff from roofs shall be by pre-calibrated tamper proof weirs; no valves or mechanical devices shall be permitted.

Exception: Scuppers are not permitted in fire walls provided in accordance with Chapter 15-8.

- 18-29-1110.3  Installation.

Runoff control shall be by control devices. Control devices shall be protected by strainers.

- 18-29-1110.4  Minimum number of roof drains.

Not less than two drains shall be installed in roof areas 10,000 square feet (930 m2) or less and not less than four roof drains shall be installed in roofs over 10,000 square feet (930 m2) in area.

- 18-29-1111  Sumps.

- 18-29-1111.1  Subsoil drains.

Subsoil drains shall be open-jointed, horizontally spill or perforated pipe conforming to one of the standards listed in Table 18-29-1102.5. Such drains shall not be less than 4 inches (100 mm) in diameter. Where the building is subject to backwater, the subsoil drain shall be protected by an accessibly located backwater valve. Subsoil drains shall discharge to a trapped sump or approved location above ground. The subsoil sump shall not be required to have either a gastight cover or a vent. Access for the purpose of cleaning and removing obstructions in subsoil drains shall be provided at every change of direction.

- 18-29-1111.2  Building subdrains.

Building subdrains located below the public sewer level shall discharge into a sump or receiving tank, the contents of which shall be automatically lifted and discharged into the drainage system as required for building sumps.

- 18-29-1111.3  Pumping system.

The sump pump, pit and discharge piping shall conform to Sections 18-29-1111.3.1 through 18-29-1111.3.4. No sump or receiving tank shall be less than 30 inches (762 mm) deep and shall be in an accessible location.

- 18-29-1111.3.1  Pump capacity and head.

The sump pump shall be of a capacity and head appropriate to anticipated use requirements.

- 18-29-1111.3.2  Construction.

An approved sump pit shall not be less than 18 inches (457 mm) in diameter and shall be constructed of vitrified clay, tile, cast iron, steel, reinforced concrete pipe, cast iron or other approved material, with a removable cover adequate to support anticipated loads in area of use. Approved plastic or fiberglass liners may be used in connection with any of the above. The pit floor or cover shall provide permanent support for the pump.

(Amend Coun. J. 3-27-02, p. 82090, § 3)

- 18-29-1111.3.3  Electrical.

Electrical service outlets, when required, shall meet the requirements of Chapter 18-27.

- 18-29-1111.3.4  Piping.

Discharge piping shall meet the requirements of Section 18-29-1102.2, Section 18-29-1102.3 or Section 18-29-1102.4 and shall include a full flow check valve. Duplex pump systems shall include a gate valve and a full flow check valve on discharge of each pump. Size and fittings shall be the same size as, or larger than, pump discharge tapping, nominal or standard sizes as designated in the referenced materials standards.

- Article 12.  Swimming Pools

- 18-29-1200  General.

- 18-29-1200.1  Scope.

This article shall apply to both private and nonprivate swimming pools. See the appropriate parts for each type.

- 18-29-1200.2  Definition – nonprivate swimming pool.

The term “nonprivate swimming pool” is hereby defined as a receptacle for water, or an artificial pool of water having a depth at any point of more than 2 feet (610 mm), intended for immersion or partial immersion therein of human beings and including all appurtenant equipment, constructed, installed, maintained anywhere in or above ground outside of a building or inside a building except in a single family dwelling unit as defined in Chapter 13-56 of the Municipal Code of Chicago.

- 18-29-1200.3  Definition – private swimming pool.

The term “private residential swimming pool” is hereby defined as a receptacle for water, or an artificial pool of water, having a depth at any point of more than 4 feet (1,220 mm), intended for the purpose of immersion or partial immersion therein of human beings, including all appurtenant equipment, constructed, installed and maintained in or above the ground outside of a building used for a single family dwelling unit. Provided that such private residential swimming pool is maintained by an individual primarily for the sole use of the owner's household and guests and not for the purpose of profit or in connection with any business operated for profit. No out-of-doors swimming pool intended for the use of members and their guests of a nonprofit club or organization, or limited to house residents of a multiple dwelling unit, a block, subdivision, neighborhood, community or other specified area of residence, shall be permitted in a single family residence, duplex residence, or apartment district.

- Part I

- 18-29-1201  Nonprivate Swimming Pools General.*

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “Generally”.

- 18-29-1201.1  Scope.

Every existing nonprivate swimming pool and every such pool constructed, installed and maintained hereafter shall comply with all applicable provisions of this chapter.

- 18-29-1201.2  Prohibited locations.

Nonprivate swimming pools shall not be permitted in single family residence districts.

- 18-29-1201.3  Permit requirements.

It shall be unlawful to proceed with the construction, installation, enlargement or alteration of any nonprivate residential swimming pool and appurtenance or bather preparation facilities within the city unless plans and specifications are submitted and a permit is first obtained from the building commissioner and commissioner of water management.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-1202  Construction.

- 18-29-1202.1  Nonprivate swimming pools.

Construction of nonprivate swimming pools shall comply with the following:

1.     Only water from the Chicago Water Works shall be used in any such pool.

2.     Such pools shall be constructed of concrete, steel or other approved materials with an impervious finish.

3.     Walk areas shall be ample in size, adequately drained, and restricted to the use of those attired for aquatic activity. There shall be adequate pitch of the walks to the drains.

4.     Walk drainage shall in no case go into the sanitary lines which drain pool overflow gutters back to the recirculation system, and shall in all cases be run independently and connect indirectly to the sewer.

- 18-29-1202.2  Recirculation inlets.

Inlets for nonprivate swimming pools shall be submerged, and be located to produce uniform circulation of water throughout the pool without the existence of dead spots, and to carry pool-bottom deposits to the outlets. This section shall be deemed to have been satisfied when the following conditions are met:

1.     Rectangular pools not exceeding 40 feet (12.19 m) by 75 feet (22.86 m) have inlets across the shallow end which serve a maximum lineal distance of 8 feet (2438 mm).

2.     Rectangular pools with outlets more than 5 feet (1525 mm) from the deep end wall are provided with additional inlets at the deep end on a maximum of 12-foot centers (3.66 m).

3.     For pools larger than 40 feet (12.19 m) by 75 feet (22.86 m) inlets are provided on not more than 20-foot (6.1 m) centers in the side walls in addition to the spacing indicated above for end wall inlet fittings.

4.     All inlets are designed as adjustable orifices, or are individually valved.

5.     All inlets discharge at a depth of 10 inches (254 mm) to 18 inches (457 mm) below the pool overflow level.

6.     Proof can be furnished to the satisfaction of the building department that adequate circulation can be obtained by other inlet arrangements, such as in the one of upward or reverse flow circulation system where inlet fittings are proposed for installation in or near the pool bottom.

- 18-29-1202.3  Outlets.

Nonprivate swimming pool outlets shall be ample in size and located at the low points of the pool. The grating areas shall be sufficient to decrease the possibility of clogging, or of suctions dangerous to the safety of the bathers. This section shall be deemed to have been satisfied when the following conditions are met:

1.     Each low point in the pool is capable of being completely drained by emptying the pool to waist line. In cases where gravity drainage cannot be accomplished an adequate pump and appurtenances are available to effect complete drainage for emptying.

2.     There are no flat areas near the outlets on which bottom deposits may accumulate.

3.     The area of the grating openings is not less than 10 times the outlet pipe area for outdoor pools.

4.     The grating is of such design that it cannot be fully removed by bathers and will not injure their fingers; and

5.     Upward or “reverse flow” circulation systems utilizing outlets in or near the shallow end overflow gutters (inlets in the deep portion) are of satisfactory hydraulic design for the adequate return of the water to the filter plant.

- 18-29-1202.4  Hose connections.

Sufficient hose connections of adequate size and supplied with sufficient water pressure shall be provided in nonprivate swimming pools for cleaning all of the pool area. This section shall be deemed to have been satisfied when the following conditions are met:

1.     Hose connections have a minimum size of 3/4 inch (20 mm) and are served by no less than a 3/4 inch (20 mm) pipe.

2.     A sufficient number of connections is provided to enable all parts of the pool area to be reached with easily manipulated hose lengths.

3.     Water pressure is sufficient to provide effective cleaning.

4.     Hose connections should be recessed, or so located as to prevent accidents.

- 18-29-1202.5  Overflow gutters.

Nonprivate swimming pools shall be entirely surrounded by overflow gutters having the necessary pitch to prevent any accumulations, having ample size to carry off normal amounts of water introduced into them, and having easy access for cleaning. This section shall be deemed to have been satisfied when the following conditions are met:

1.     The overflow gutter extends around the entire perimeter of the pool; the overflow gutter edge is level within 2/10 inch (5 mm) on pools smaller than 40 feet (12.2 m) by 85 feet (25.9 m) and 2/10 inch (eight mm) on larger installations.

2.     The overflow gutter bottom has a pitch of not less than 3 inches (75 mm) in 10 feet (3.05 m).

3.     The drains are a maximum of 15 feet (4.57 m) on centers.

4.     The runoff capacity is sufficient to carry away all normal amounts of water splashed or displaced into them without flooding of the overflow gutter.

5.     The overflow gutter has a minimum depth of 4 inches (100 mm).

6.     The overflow gutter is of the open, roll-over or semiprocessed type, having a smooth finish and having an opening sufficient to permit satisfactory cleaning of the overflow channel.

7.     Overflow drains that discharge to a sewer have a free-fall discharge with an atmospheric break of 2 inches (50 mm) minimum.

8.     Drain lines shall be at least 2 1/2 inches (64 mm) in diameter.

9.     Satisfactory proof can be furnished to the buildings department that adequate runoff capacity will be obtained by other arrangements or modifications in gutter design proposed for use in “closed” or reverse flow systems of recirculation.

Exceptions:

1.     At pools having a water surface area of 1,500 square feet (139.35 m2) or less and which are expected to have only light skimmer loading, automatic surface skimmers may be provided in lieu of overflow gutters in the proportion of one skimmer per each 500 square feet (46.45 m2) or fraction thereof. Such skimmers shall be built into the wall and have an automatically controlled equalizer pipe to prevent air- lock in the suction line.

2.     Skimmer return piping shall be not less than 2 inches (50 mm) in diameter. The equalizer pipe shall be not less than 2 inches (50 mm) in diameter and be located at least 1 foot (300 mm) below the lowest overflow level of the skimmer.

- 18-29-1202.6  Equipment for removal of sediment.

The nonprivate swimming pool shall be provided with equipment to remove sediment and other accumulations from the bottom of the pool. This pool equipment shall comply with the following requirements:

1.     The pool shall be provided with a satisfactory suction cleaner system of either the built-in or portable type (built-in types are preferable).

2.     Sufficient suction and capacity shall be provided to remove all normal accumulations from the pool bottom.

3.     Vacuum pipes shall be 3 inches (76 mm) minimum diameter, and vacuum hoses shall be 2 inches (51 mm) minimum diameter.

4.     Vacuum fittings shall be installed at 8 inches (203 mm) below normal water level in the pool.

- 18-29-1202.7  Recirculation system.

The recirculation system in a nonprivate swimming pool shall consist of pumping equipment, hair and lint catcher, and filters, together with all necessary pipe connections to the inlets and outlets of the pool and for backwashing the filters. As an integral part of the system, equipment shall be provided for disinfecting the water and adding any necessary chemicals and make-up water.

- 18-29-1202.7.1  Turnover of pool contents.

The entire system and all its component parts shall be capable of producing a six-hour turnover of the entire contents of the pool. Recirculation system piping shall be of the materials indicated in Article 7, with the exception that they may be constructed of Schedule 40 PVC.

- 18-29-1202.8  Equipment required.

Adequate pumping equipment shall be provided in every nonprivate swimming pool. Pumping equipment shall be provided in accordance with the following:

1.     The pump has sufficient capacity to discharge the volume of water required for a six-hour turnover of the pool against the maximum head in the recirculation system.

2.     The pump used for backwashing sand filters has sufficient capacity to backwash a filter unit at the rate of at least 15 gallons per minute per square foot (56.8 lpm/0.09 m2) of filter area.

3.     The pump develops a good suction when the pipes for a suction cleaner are connected to the recirculation system.

4.     A compound vacuum-pressure gauge is installed on the recirculation pump suction line; and a pressure gauge on the pump discharge line.

- 18-29-1202.9  Strainer required.

Every nonprivate swimming pool shall be provided with a hair and lint catcher of acceptable design on the suction side of the recirculation pump, except where pump suction is connected to the underdrains of a filter system. Swimming pool strainers shall comply with the following requirements:

1.     The hair and lint catcher as installed ahead of the recirculation pump.

2.     The strainer is located so as to be easily accessible for cleaning.

3.     Two strainer baskets are provided for alternate use in each unit.

4.     Water passes through the strainer from the outside.

5.     The strainer is made of non-corrosive material.

6.     The width or diameter of the strainer openings is not more than 1/8 inch (3 mm).

7.     The area of the strainer openings is five to ten times the area of the inlet pipe to the strainer.

8.     The hair and lint catcher is so constructed that it can easily and quickly be taken down for cleaning.

9.     A removable cylindrical strainer, with slotted openings, is provided unless sufficient cause can be shown for using some other type.

- 18-29-1202.10  Disinfection equipment.

Every non-private swimming pool shall be provided with equipment for the adequate disinfection of all pool water. This requirement shall be deemed to have been satisfied when the following conditions are met:

1.     Chlorine, chlorine compounds, or bromine are used as disinfectants.

2.     The disinfection equipment has sufficient capacity to feed up to three parts per million of available disinfectant at indoor pool installations based upon the recirculation rate.

3.     The capacity at outdoor pools has a feed rate of up to eight parts per million based on the recirculation rate. This capacity shall be increased where abnormally high demands are encountered.

4.     The disinfectant is introduced into the recirculation system ahead of the filters where sand media is employed.

- 18-29-1202.11  Chemical equipment.

The system of every nonprivate swimming pool shall include equipment for the introduction of chemicals necessary for maintaining the pool water in proper balance chemically and the application of a compound, such as alum coagulant, to form a filter aid-floc on the surface of sand filter beds. This requirement shall be deemed to have been satisfied when the chemical feed equipment is convenient to use and has proper capacity to produce intended results when adjusted for the specific chemical solution being applied.

- 18-29-1202.11.1  Coagulant solutions.

If a coagulant solution is to be applied, the point of application is far enough ahead of the sand filters to obtain a thorough mix with the water flowing in the recirculation piping.

- 18-29-1202.12  Filtration equipment.

Filtration equipment shall be provided on all nonprivate swimming pools. Filtration equipment shall be provided in accordance with Section 18-29-1202.12.1 through Section 18-29-1202.12.9.

- 18-29-1202.12.1  Filter area.

Sufficient filter area is provided to filter the entire contents of the pool in six hours at the rate of not more than 3 gallons per square foot (11.36 L/0.09 m2) per minute.

- 18-29-1202.12.2  Underdrain system size.

The standard type underdrain system used in the gravel bed is at least 12 inches (305 mm) in depth and varies in gravel size from approximately 1 1/2 inches (38 mm) at the bottom to approximately 1/8 inch (3 mm) at the top.

- 18-29-1202.12.3  Filter sand depth.

The filter sand depth is not less than 20 inches (508 mm), the effective grain size is between 0.45 and 0.55 millimeters; the uniformity coefficient does not exceed 1.6, and there is sufficient distance between the top of the filter to the point of discharge of the wash water to allow for filter media expansion during the back washing at the specified rate without loss of filter media.

- 18-29-1202.12.4  Loss-of-head gauges.

Loss-of-head gauges are installed on each gravity filter.

- 18-29-1202.12.5  Proper design.

The underdrain system is properly designed to collect efficiently the filtered water and to distribute properly the backwash water at a rate of not less than 15 gallons per minute per square foot (56.8 lpm/0.09 m2) of filter area.

- 18-29-1202.12.6  Pressure sand filter system provisions.

The pressure sand filter system shall be provided with:

1.     Gauges for each battery on the inlet and outlet pipes for determining loss-of-head in filter media.

2     Air releases with a manual control on the highest point of each filter.

3.     A readily removable head or a large manhole to facilitate inspection and repairs.

4.     A rate-of-flow indicator having satisfactory range shall be provided. It should be located in the recirculation line so that the rate of flow either during normal circulation or during the filter backwashing operation can be determined.

- 18-29-1202.12.7  Filter media other than sand.

When filter media other than sand is employed, special requirements must be satisfied. The process involving filtration through a coating of filter-aid material such as diatomaceous earth on porous tubes or elements is satisfactory when the following conditions are met:

1.     Sufficient element surface area is provided to filter the entire contents of the pool in six hours at the rate of 2 gallons or less per minute per square foot (7.57 lpm/0.09 m2).

2.     Slurry feeding equipment is provided for the continuous application, at an accurate and uniform rate, of filter-aid material into the filter influent line.

Exception: Such feeders may be omitted at pools where filter-aid units have sufficient element surface area to filter the pool volume in six hours at a rate not to exceed 1 1/2 gallons per square foot (5.68 L/0.09 m2) per minute.

1.     Pressure gauges are installed on both the influent and the effluent side of each filter unit.

2.     A rate-of-flow indicator properly located and having satisfactory range is provided on the effluent line from the filters.

3.     Sufficient head room and facilities are available in the filter room for periodic removal of the filter head and element assembly for manual cleaning purposes.

- 18-29-1202.12.8  Sight glass.

An easily removed sight glass is required on the waste discharge line (unless the washwater discharge is plainly visible) for indicating the progress in filter- washing or the clarity when filtering-to-waste.

- 18-29-1202.12.9  Filter piping arrangement.

The filter piping arrangement is as simple as possible to accomplish filtration, backwashing, and filtering-to-waste. Sand filter units designed for performance at high rates of filtration are acceptable for installation at pools of small to moderate size and which are planned to accommodate only light swimmer loading; provided further, that such filter units have been tested and approved by a nationally recognized testing laboratory to function satisfactorily at the rate or rates specified. If a high-rate sand filter unit installed at a swimming pool fails to produce results satisfactory to the department it must be replaced with an adequate and approved filter unit of conventional design.

- 18-29-1202.13  Make-up water.

All nonprivate swimming pools shall be equipped with provisions for adding make-up water. Only water from the Chicago Waterworks System shall be used for make-up water.

- 18-29-1202.14  Sewage or waste water.

No piping arrangements shall exist which under any conditions will permit sewage or waste water to enter the recirculation system, or water from the recirculation system or pool to enter the make-up water supply. This requirement shall be deemed to have been satisfied when the following conditions are met:

1.     No pipe furnishing water for the make-up water supply is physically connected to the recirculation system regardless of valve arrangements, unless an approved vacuum breaker is properly installed on the make-up water line.

2.     The make-up water line discharging directly to the pool has its point of discharge at least 6 inches (152 mm) above the walk area adjacent to the pool.

3.     The make-up water line discharging to a surge or balancing tank has its point of discharge at least 6 inches (152 mm) above the rim of the tank.

4.     The main drain line, and the filters' backwash and filter-to-waste lines have a free-fall discharge to the sewer or drain at such elevation that a surcharged sewer or drain could not force contamination back into the pool or recirculation system.

5.     All other accessories to the recirculation system such as chemical solution feeders, water-fed chlorinators, etc., are protected against back siphonage into the water supply.

- 18-29-1202.15  Cleanouts.

Cleanouts shall be provided at such points in the recirculation system as will enable obstructions, accumulations, debris, etc., to be readily removed.

- 18-29-1202.16  Accessibility.

Filters and other equipment shall be accessible. This requirement shall be deemed to have been satisfied when the recirculation equipment is conveniently located for inspection and servicing. Special attention is called to the necessity of providing adequate head room above pressure filters.

- 18-29-1202.17  Hydrogen-ion concentration.

Every nonprivate swimming pool shall be provided with an outfit for the determination of hydrogen-ion concentration; this requirement shall be deemed to have been satisfied when an approved outfit for the determination of hydrogen-ion concentration in the pH range 6.8 to 8.0 is provided.

- 18-29-1202.18  Disinfectant residuals.

Every nonprivate swimming pool shall be provided with an outfit for the determination of disinfectant residuals. This item shall be deemed to have been satisfied when an approved outfit for the determination of residuals in the range zero to two parts per million is provided.

- 18-29-1203  Additional Facilities Required.

- 18-29-1203.1  Equipment room location and drainage.

The equipment room for every nonprivate swimming pool shall be satisfactorily located and adequately drained. This requirement shall be deemed to have been satisfied when the following conditions are met:

1.     The equipment room is so located that it cannot be entered directly from shower rooms or pool area.

2.     The floor has a minimum pitch of 3 inches (75 mm) in 10 feet (3.05 m) toward the drains with no low spots which will allow water to stand.

3.     The equipment room drains do not discharge to a sewer or drain which may surcharge onto the equipment room floor.

- 18-29-1203.2  Dressing room drainage.

Dressing rooms for every nonprivate swimming pool shall be satisfactorily drained. This requirement shall be deemed to have been satisfied when the following conditions are met:

1.     The dressing rooms are located adjacent to the locker or check room and showers.

2.     Floors have a minimum pitch of 3 inches (75 mm) in 10 feet to the drains with no low spots which will allow water to stand.

3.     Hose bibs of 3/4 inch (20 mm) minimum size and served by not less than a 3/4 inch (20 mm) pipe are provided to enable the entire dressing room to be conveniently flushed by hose.

- 18-29-1203.3  Shower facilities.

Adequate and satisfactorily designed and located shower facilities, including warm water and soap, shall be provided for every nonprivate swimming pool. This requirement shall be deemed to have been satisfied when the following conditions are met:

1.     Separate shower facilities are provided for men and women and are so located that bathers must pass from the shower room directly to the pool area.

2.     Shower facilities for pools used by groups, classes or platoons on a regular time schedule of 1 hour or less have one shower for each four bathers in the maximum class or one shower for each 10 if the period is two hours. Shower facilities for pools with continuous bathing have a minimum of one shower for each 40 bathers expected at the time of maximum load.

3.     The ceilings, walls, and floors of the shower room or area are constructed of impervious material not adversely affected by steam or water.

4.     The floor is smooth, nonslip to bare feet, has no open cracks or joints, and has a minimum pitch of 3 inches (75 mm) in 10 feet (3.05 m) toward the drains with no low spot which will allow water to stand.

5.     A minimum of 3 gallons (11.36 L) of water per shower per minute, having a temperature of not less than 90°F (32.2°C) is provided.

6.     The showers are so designed that a proper mixture of hot and cold water may be obtained without danger of scalding the bather.

7.     Liquid or powdered soap in suitable dispensing equipment is provided for each shower unit.

8.     Shower booths are provided in the women's shower room, with partitions that will not be damaged by the shower water and which will have a minimum clearance of 6 inches (150 mm) above the floor.

9.     Shower drainage is discharged to the sanitary sewerage system.

- 18-29-1203.4  Toilet facilities.

Adequate, satisfactory, and properly located toilet facilities of acceptable design shall be provided in every nonprivate swimming pool. Toilet facilities shall be provided in accordance with Sections 18-29-1203.4.1 through 18-29-1203.4.3.

- 18-29-1203.4.1  Inside dry.

Toilets known as “inside dry” for both genders are provided for the patrons in the dressing area, to which toilets they may have convenient access without crossing floors or using fixtures wet from bathers.

- 18-29-1203.4.2  Inside wet.

Toilets known as “inside wet” for each gender are provided for the patrons while in the shower rooms or pool area, to which toilets they may have access without crossing areas used by persons in street shoes.

- 18-29-1203.4.3  Fixtures.

Fixtures must comply with the numbers specified in Table 18-29-1203.4.3.1 and Table 18-29-1203.4.3.2.

- 18-29-1203.4.3.1  Smaller pools.

Pools not larger than 50 feet (15.24 m) by 100 feet (30.48 m) in area with a permissible bathing load not to exceed 700 persons shall comply with the specifications listed in Table 18-29-1203.4.3.1.

Table 18-29-1203.4.3.1
Maximum Pool Area 50 ft. by 100 ft.

Gender; Inside Dry; Inside Wet. Men; 2 closets; 1 closets. 2 urinals; 1 urinal. 1 lavatory; 1 lavatory. Women; 3 closets; 2 closets. 1 lavatory; 1 lavatory.

- 18-29-1203.4.3.2  Larger pools.

Pools larger than 50 feet (15.24 m) by 100 feet (30.48 m) in area with a permissible bathing load of over 700 persons shall comply with the specifications listed in Table 18-29-1203.4.3.2.

Table 18-29-1203.4.3.2
Pools Larger than 50 ft. by 100 ft.

Gender; Inside Dry; Inside Wet. Men; 3 closets; 2 closet. 4 urinals; 2 urinals. 2 lavatories; 1 lavatory. Women; 4 closets; 2 closets. 2 lavatories; 1 lavatory.

- 18-29-1203.4.4  Deliberately omitted.

- 18-29-1203.4.5  Backsiphonage.

All fixtures shall be protected against backsiphonage.

- 18-29-1203.4.6  Cleaning.

All fixtures shall be so designed that they may be readily cleaned, and that frequent cleaning and disinfection will not damage them.

- 18-29-1203.4.7  Splashing.

Urinals in the inside wet toilet shall be of a type which will not cause splashing of urine upon the feet and legs of bathers.

- 18-29-1203.4.8  Floors.

Toilet floors shall be constructed of impervious material with no open cracks or joints, have a smooth nonslip finish, and pitch not less than 3 inches (75 mm) in 10 feet (3.05 m) toward the drains.

- 18-29-1203.4.9  Hose bibs.

Hose bibs shall be not less than 3/4 inch (20 mm) size, and shall be served by not less than 3/4 inch (20 mm) pipe, for convenient hosing of the toilet rooms or area.

- 18-29-1203.4.10  Discharge.

Toilet room sewage shall be discharged to the sanitary sewerage system.

- 18-29-1203.5  Subsurface drainage.

All nonprivate swimming pools shall have adequate subsurface drainage not directly connected to a sewer. When gravity subsurface drains are not possible, the drainage should be into a sump, and provisions made to insure its proper functioning during the off-season of an outdoor pool.

- 18-29-1203.6  Drinking fountains.

At each nonprivate swimming pool, drinking fountains shall be provided in the pool area, in the dressing rooms, and for the spectators. Any fountains that are provided must meet recognized sanitary design features. The fountain should be recessed or located so as to prevent accidents.

- 18-29-1203.7  Bathhouse facilities at apartment pools.

A bathhouse with facilities for each gender shall be installed in accordance with Sections 18-29-1203.7.1 through 18-29-1203.7.2.

- 18-29-1203.7.1  Where required.

The number of showers and toilet fixtures which shall be made available depends on the pool size and the number of families in the apartment group, as illustrated in Table 18-29-1203.7.1.

Table 18-29-1203.7.1
Bathhouse Facilities at Apartment Pools

No. of Units/Pool Size; Gender; Facilities Requirements. Less than 72 units; Men:; 1 closet. 1 shower. Pool size:; 1 lavatory. small; Women:; 1 closet. 1 shower. 1 lavatory. 72 to 125 units; Men:; 2 closets. Light bathing load; 2 showers. 1 lavatory. Pool size:; Women:; 2 closets. small to medium; 2 showers. 1 lavatory. More than 125 units; See Sections 18-29-1203.4 through 18-29-1203.4.10.. Pool size: medium to large.

Exception: An exception to this requirement is an indoor pool which serves residents of 10 or less living units and which units are all located in the same building as the swimming pool structure and on a level not greater than three stories difference in elevation from the pool level.

- 18-29-1203.7.2  Outdoor pools.

A small bathhouse with facilities for each gender shall be installed adjacent to, or within 50 feet (15.24 m) of an outdoor nonprivate swimming pool serving residents of an apartment when:

1.     The farthest apartment from the pool in a one- story apartment group is more than 275 feet (83.82 m) away.

2.     The farthest apartment from the pool in a two- story apartment groups is more than 225 feet (68.58 m) away.

3.     The farthest apartment in a three-story apartment group is more than 175 feet (53.34 m) away.

4.     The apartment building is four or more stories in height.

- 18-29-1203.7.3  Indoor pools.

Bathhouse facilities for each gender shall be installed adjacent to each indoor nonprivate swimming pool, whether saving multi-story condominium apartment units within the same building structure as the pool, or serving apartments in a group of outlying buildings clustered around the swimming pool structure.

- Part II

- 18-29-1204  Private Swimming Pools.

- 18-29-1204.1  Location.

Private swimming pools shall be located in accordance with Sections 18-29-1204.1.1 through 18-29-1204.3.

- 18-29-1204.1.1  District limitations.

Private residential swimming pools shall be permitted in single family residence districts only.

- 18-29-1204.1.2  Distance from property line.

No portion of a private residential swimming pool shall be located at a distance less than 10 feet from any side or rear property line, or building line. Pumps, filters and pool water disinfection equipment installations shall be located at a distance not less than 10 feet (3.05 m) from any side property line.

- 18-29-1204.2  Permit required.

It shall be unlawful to proceed with the construction, installation, enlargement or alteration of any private residential swimming pool and appurtenances within the city unless permits therefor shall have first been obtained from the building commissioner and the commissioner of water management.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-1204.3  Drawings, plans and permits.

Drawing,* plans and permits shall meet specific standards in accordance with Sections 18-29-1204.3.1 through 18-29-1204.3.4.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, §1; correct language appears to be “Drawings”.

- 18-29-1204.3.1  Presentation, examination and approval.

All drawings and plans for the construction, installation, enlargement or alteration of any private residential swimming pool and appurtenances for which a permit is required shall be first presented to the building commissioner for the examination and approval as to proper location, construction, and use, and thereafter shall be presented to the health commissioner and the commissioner of water management for examination and approval.  After said drawings and plans have been examined and passed upon, the same shall be returned to the building commissioner for examination and approval.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-1204.3.2  Scale and dimensions of plan.

All plans and drawings shall be drawn to a scale of not less than 1/8 inch to the foot (1:100 SI), on paper or cloth in ink, or by some process which will not fade or obliterate. All distances and dimensions shall be accurately figured and drawings made explicit and complete, showing the lot lines, and including information pertaining to the pool, walk and fence construction, water supply system, drainage and water disposal systems, and all appurtenances pertaining to the swimming pool. Detained plans and vertical elevations shall be provided.

- 18-29-1204.3.3  Restrictions prior to issuance of permit.

No person shall construct, enlarge, alter or use any private residential pool and appurtenances until plans have been examined and approved by the board of health, the department of water management and the department of buildings and the necessary approvals are issued by the department of water management and the department of buildings.

(Amend Coun. J. 3-5-03, p. 104990, § 48; Amend Coun. J. 11-13-07, p. 14999, Art. II, § 1)

- 18-29-1204.3.4  Deviation from plans.

All private residential swimming pools, appurtenances, water supply and drainage systems shall be constructed in conformity with the approved plans. If any deviation from such plans is desired, a supplementary plan covering that portion of the work involved shall be filed for approval and shall conform to the provisions of this chapter.

- 18-29-1204.4  Recirculation pools.

All private residential swimming pools shall be of the recirculation type in which circulation of the water is maintained through the pool by pumps; the water drawn from the pool being clarified and disinfected before being returned to the pool.

- 18-29-1204.5  Materials.

Private residential swimming pool walls and floor shall be constructed of any impervious material which will provide a tight tank and white or light-colored easily-cleaned surfaces. The side and end walls shall be vertical and shall present a smooth finish. The floor or bottom surface of the pool shall have a non-slip finish as smooth as possible.

- 18-29-1204.6  Structural design.

The structural design and construction of private residential swimming pools shall comply with the structural sections of the building code. Pools shall be designed to withstand the water pressure from within and to resist the pressure from the earth when the pool is empty. The slope of the bottom of any part of the pool in which the water is less than 5 feet (1525 mm) in depth shall not be more than 1 foot (300 mm) in each 15 feet (3.95 m). The maximum slope where the water is 5 feet (1525 mm) or more in depth shall not exceed 1 foot (300 mm) in 3 feet (915 mm).

- 18-29-1204.7  Walk areas.

Unobstructed walk areas not less than 6 feet wide shall be provided to extend entirely around the pool. The walk area shall be constructed of impervious material and the surfaces shall be such as to be smooth and easily cleaned and of non-slip construction. The slope of the walks shall have a pitch of at least 1/4 inch (6 mm) to the foot (300 mm), designed so as to prevent back drainage from entering the pool. Walk drains shall be provided for each 100 square feet (9.29 m2) of walk area. Drain pipe lines shall be at least 3 inches (75 mm) in diameter, drain openings shall have an open air of at least four times the cross-sectional area of the drain pipe. The walk drain systems shall have an indirect connection to the sewer. The walk drains shall not be connected to the recirculation system piping. The drainage system shall be constructed of materials in conformance with Article 7 of this chapter, with the exception that all drainage and recirculation piping may be Schedule 40 PVC.

- 18-29-1204.8  Fences.

All private residential swimming pools shall be completely enclosed by a fence erected along the perimeter of the pool walks. All fence openings or points of entry into the pool enclosure shall be equipped with gates. The fence and gates shall be 5 feet (1525 mm) in height above the walk grade level and shall be constructed of a minimum number 9 gage woven wire mesh corrosion-resistant material. All gates shall be equipped with self-closing and self-latching devices placed at the top of the gate and made inaccessible to small children. All fence posts shall be decay- or corrosion-resistant and shall be set in concrete bases.

- 18-29-1204.9  Steps or ladders.

Two or more means of egress in the form of steps, ladders, or step holes shall be provided for all private residential pools. At least one such means of egress shall be located on a side of the pool at both the deep end and shallow end of the pool. Treads of steps, ladders or step holes shall be constructed of non-slip material and at least 3 inches (75 mm) wide for their full length. Steps, ladders or step holes shall have a handrail on both sides.

- 18-29-1204.10  Overflow gutters.

Private residential swimming pools shall be provided with overflow gutters on all vertical walls and shall extend around the entire perimeter of the pool. The overflow gutter shall be of the open, roll over or semi- recessed type, having a smooth finish. The lip or overflow gutter edge shall be level, the overflow gutter shall have a minimum depth of 4 inches (100 mm); the overflow gutter bottom shall have a slope toward each drain and have a pitch not less than 1/4 inch (6 mm) to the foot (300 mm); drain spacings shall be a minimum of 15 feet (3.95 m) on centers; drain pipelines shall be at least 3 inches (75 mm) in diameter; outlet fixtures shall have a grate opening of at least twice the cross-sectional area of the drain pipe; the drain lines shall have an indirect connection to the sewer. The drainage system shall be constructed in accordance with Article 7 of this chapter.

- 18-29-1204.11  Water supply.

No source of water other than that secured from the Chicago Waterworks System shall be used in private residential swimming pools.

- 18-29-1204.12  Inlets.

All water recirculation system inlets and makeup water facilities shall be located, equipped and constructed in accordance with Section 18-29-1204.13.1 through 18-29-1204.13.3.

- 18-29-1204.12.1  Water recirculation system inlets.

Private residential swimming pool water recirculation system inlet shall be located so as to produce as far as possible uniform circulation throughout the pool without the existence of dead spots and to carry pool bottom deposits to the outlets. Recirculation systems inlets in the pool walls shall be spaced not more than 20 feet (6.10 m) on centers entirely around the perimeter of the pool and shall discharge at a minimum depth of 10 inches (254 mm) below the pool overflow level.

- 18-29-1204.12.2  Makeup water.

Pools shall be equipped with suitable facilities for adding makeup water as needed. There shall be no physical connection between the water supply line and the pool system. If the makeup water is added directly to the pool, the outlet shall be at least 6 inches (150 mm) above the upper rim of the pool. If the makeup water line discharges to a surge or balancing tank, the point of discharge shall be at least 6 inches (150 mm) above the run of the tank. If a hose connection from a sill cock or other plumbing fixture is to be used for supplying makeup water, then an approved vacuum breaker shall be installed between the sill cock or control valve at the fixture and the hose connection. The vacuum breaker shall be installed at a height not less than 7 feet 6 inches (2286 mm) above the floor, platform or ground upon which a person would stand when operating a sill cock or control valve.

- 18-29-1204.12.3  Water systems construction conformance.

The systems supplying recirculated water and makeup water to the pool shall be constructed in conformance with Article 6 of this chapter, with the exception that the system supplying recirculated water can utilize Schedule 40 PVC pipe.

- 18-29-1204.13  Outlets.

All water recirculation system outlets and water discharge facilities shall be located, equipped and constructed in accordance with Sections 18-29-1204.14.1 through 18-29-1204.14.3.

- 18-29-1204.13.1  Water recirculation system outlets.

Private residential swimming pool water recirculation system outlets shall be so located as to provide at least one outlet at the deepest point of the pool, if the pool width does not exceed 20 feet (6.10 m). If the pool width is more than 20 feet (6.10 m), multiple outlets shall be provided and spaced not more than 20 feet (6.10 m) apart, nor more than 10 feet (2.63 m) from the walls. All pool drain outlets shall be equipped with gratings having an area of openings not less than 10 times the cross-sectional area of the outlet pipe. The grating shall be of such design that cannot be readily removed by bathers and will not injure bather's fingers.

- 18-29-1204.13.2  Drainage system.

Pools shall be equipped with facilities for completely emptying the pool and the discharge from the pool water to the sewer shall be at a rate not exceeding 250 gallons (946 L) per minute. No direct connection shall be made to the sewer. The drainage system shall be constructed in conformance with Article 7. The drain pipe line diameter shall be at least 6 inches (150 mm).

- 18-29-1204.13.3  Drain water discharge.

Drain pipe lines from the walk areas, scum gutters and pools shall discharge into a common catch basin. If elevation permits, the catch basin may drain by gravity into the sewer. If, however, the elevations are such as to require pumping, the combined discharge shall be pumped into the sewer. In either case, a back water valve or gate shall be installed downstream from the catch basin and the pump. Water drained from the pool shall not be discharged to the sewer system during periods of rain or storms. At no time shall the rate of drain water discharge exceed 250 gpm (209 Lpm).

- 18-29-1204.14  Recirculation system and appurtenances.

Private residential swimming pool recirculation systems and appurtenances shall comply with the standards specified in Sections 18-29-1204.14.1 through 18-29-1204.14.8.

- 18-29-1204.14.1  Required apparatuses.

Private residential swimming pool recirculation systems shall consist of pumping equipment, hair and lint catchers, filter, together with the necessary pipe connections to the pool inlets and outlets, facilities and pipe connections necessary for backwashing filters, and facilities and equipment for disinfecting the pool water.

- 18-29-1204.14.2  Water volume turnover.

The entire recirculating system shall be capable of producing a six-hour turnover of the entire water volume contents.

- 18-29-1204.14.3  Pump capacity.

The recirculation system pump shall have sufficient capacity to discharge the volume of water required for a six-hour turnover of the pool against the maximum head in the recirculating system.

- 18-29-1204.14.4  Backwash filter rate.

The pump used for backwashing filters shall have sufficient capacity to provide a backwash filter rate of at least 15 gpm per square foot (56.8 lpm/0.09 m2) of filter area.

- 18-29-1204.14.5  Hair and lint strainer.

A hair and lint catcher or strainer shall be installed on the suction side of the circulation pump to prevent hair, lint and other extraneous material from reaching the pump filters. Hair and lint catchers shall be so designed that they can be easily dismantled for cleaning and inspection and shall be so located as to be easily accessible for cleaning. The design features shall be as follows: Water passes through the strainer from the outside; the strainer is made of non-corrosive material; the width or diameter of the miner openings is not more than 1/8 inch (3 mm); the area of the strainer openings shall be at least five times the cross sectional area of the inlet pipe to the strainer.

- 18-29-1204.14.6  Pressure filters.

Recirculating systems shall contain rapid pressure filters. Sufficient filter area shall be provided to filter the entire contents of the pool in six hours at the rate of not more than 3 gallons per square foot (11.4 L/.09 m2) filter area per minute. The filter backwashing facilities shall be sufficient to backwash at the rate of 15 gallons per minute (12.5 L/0.09 m2) filter area. All backwash water and effluents shall be discharged to the sewer through an indirect connection. Pressure filters shall be equipped with readily accessible air relief valves, loss of head or pressure gauges on the inlet and outlet pipes, and an access head or hole large enough to permit inspection, maintenance and repair work. Sight glasses that can be easily removed for cleaning shall be provided in the effluent line from the filter units.

- 18-29-1204.14.7  Disinfection equipment.

Equipment shall be provided for the disinfection of all pool water. Any disinfection method using materials other than chlorine compounds shall be subject to the approval of the board of health. Disinfection equipment installed for the use of chlorine compounds shall have sufficient capacity to maintain a minimum free chlorine residual of 0.5 parts per million. The disinfectant shall be introduced into the recirculation system ahead of the filters.

- 18-29-1204.14.8  Gaseous chlorination systems.

Gaseous chlorination systems shall not be made use of as a disinfection method for pool water.

- 18-29-1204.15  Electrical installations.

All electrical installations provided for, installed and used in conjunction with private residential swimming pools shall be in conformance with Chapter 18-27 Electrical code.

- 18-29-1204.16  Maintenance.

All private residential swimming pools shall be maintained in a satisfactory operating condition during the periods the pool is in use.

- 18-29-1204.17  Inspection.

The board of health periodically shall inspect all private residential swimming pools to determine whether or not the provisions of this code regarding health, sanitation and safety applicable thereto are being complied with.

- Article 13.  Referenced Standards

NOTE: Add the prefix 18-29- to all cited sections and tables

This article lists the standards that are referenced in various sections of this document. The standards are listed herein by the promulgating agency of the standard, the standard identification, the effective date and title, and the section or sections of this document that reference the standard. The application of the referenced standards shall be as specified in Section 18-29-102.8.

| ANSI | American National Standards Institute 11 West 42nd Street New York, NY 10036 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| Z21.22-86 | Relief Valves and Automatic Gas Shutoff Devices for Hot Water Supply Systems – with 1990 Addendum | 502.4, 504.5 |
| Z124.1-95 | Plastic Bathtub Units | 407.1 |
| Z124.2-95 | Plastic Shower Receptors and Shower Stalls | 417.1 |
| Z124.3-95 | Plastic Lavatories | 416.1, 416.2 |
| Z124.4-86 | Plastic Water Closet Bowls and Tanks | 420.1 |
| Z124.6-90 | Plastic Sinks | 415.1, 418.1 |
| Z358.1-98 | Emergency Eyewash and Shower Equipment | 411.1 |

| ARI | Air-Conditioning & Refrigeration Institute 4301 N. Fairfax Drive, Suite 425 Arlington, VA 22203 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| 1010-94 | Self-Contained, Mechanically-Refrigerated Drinking-Water Coolers | 410.1 |

| ASME | American Society of Mechanical Engineers 345 East 47th Street New York, NY 10017 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| A13.1-81 | Scheme for the Identification of Piping Systems | 608.8 |
| A112.1.2-91 | Air Gaps in Plumbing Systems | Table 608.1 |
| A112.6.1-88 | Supports for Off-the-Floor Plumbing Fixtures for Public Use | 405.4.3 |
| A112.14.1-75 | Backwater Valves | 504.7.3, 715.3 |
| A112.18.1M-94 | Brass Plumbing Fixture Units – with 1995 Errata | 424.1 |
| A112.19.1M-94 | Enameled Cast Iron Plumbing Fixtures | 407.1, 410.1, 415.1, 416.1, 418.1 |
| A112.19.2-95 | Vitreous China Plumbing Fixtures – with 1996 Errata | 408.1, 410.1, 416.1, 418.1, 419.1, 420.1 |
| A112.19.3-87 | Stainless Steel Plumbing Fixtures (Designed for Residential Use) | 415.1, 416.1, 418.1 |
| A112.19.4M-94 | Porcelain Enameled Formed Steel Plumbing Fixtures | 407.1, 416.1, 418.1 |
| A112.19.5-79 | Trim for Water-Closet Bowls, Tanks, and Urinals | 425.4 |
| A112.19.6-95 | Hydraulic Performance Requirements for Water Closets and Urinals | 419.1, 420.1 |
| A112.19.7-95 | Whirlpool Bathtub Appliances | 421.1 |
| A112.19.8-87 | Suction Fittings for Use in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Whirlpool Bathtub Appliances | 421.4 |
| A112.19.9-91 | Non-Vitreous Ceramic Plumbing Fixtures | 407.1, 408.1, 410.1, 415.1, 416.1, 417.1, 418.1, 420.1 |
| A112.21.1-91 | Floor Drains | 412.1 |
| A112.21.2-91 | Roof Drains | 1102.6 |
| B1.20.1-83 | Pipe Threads, General Purpose (inch) | 605.12.3, 605.16.3, 605.16.3, 605.17.1, 705.4.3, 705.7.4, 705.10.1, 705.12.3 |
| B16.3-92 | Malleable Iron Threaded Fittings | Table 605.6, Table 702.4 |
| B16.4-92 | Cast Iron Threaded Fittings | Table 605.6, Table 702.4 |
| B16.9-93 | Factory-Made Wrought Steel Buttwelding Fittings | Table 605.6, Table 702.4 |
| B16.11-91 | Forged Steel Fittings, Socket-Welding and Threaded | Table 605.6, Table 702.4 |
| B16.12-91 | Cast-Iron Threaded Drainage Fittings | Table 605.6, Table 702.4 |
| B16.15-85 | Cast Bronze Threaded Fittings | Table 605.6, Table 702.4 |
| B16.18-84 | Cast Copper Alloy Solder Joint Pressure Fittings | Table 605.6, Table 702.4 |
| B16.22-95 | Wrought Copper and Copper Alloy Solder Joint Pressure Fittings | Table 605.6, Table 702.4 |
| B16.23-92 | Cast Copper Alloy Solder Joint Drainage Fittings (DWV) – with 1994 Errata | Table 605.6, Table 702.4 |
| B16.26-88 | Cast Copper Alloy Fittings for Flared Copper Tubes | Table 605.6, Table 702.4 |
| B16.28-94 | Wrought Steel Buttwelding Short Radius Elbows and Returns | Table 605.6, Table 702.4 |
| B16.29-94 | Wrought Copper and Wrought Copper Alloy Solder Joint Drainage Fittings – DVW | Table 605.6, Table 702.4 |
| B16.32-92 | Cast Copper Alloy Solder Joint Fittings for Solvent Drainage Systems | Table 605.6, Table 702.4 |

| ASSE | American Society of Sanitary Engineering 28901 Clemens Road Westlake, OH 44145 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| 1001-90 | Performance Requirements for Pipe Applied Atmospheric Type Vacuum Breakers | 425.2, Table 608.1 |
| 1002-86 | Performance Requirements for Water Closet Flush Tank Ball Cocks | 425.3.1, Table 608.1 |
| 1003-95 | Performance Requirements for Water Pressure Reducing Valves for Domestic Water Supply Systems | 604.8 |
| 1004-90 | Performance Requirements for Commercial Dishwashing Machines | 409.1 |
| 1005-86 | Performance Requirements for Water Heater Drain Valves – with 1986 Revision | 501.3 |
| 1006-89 | Performance Requirements for Residential Use (Household) Dishwashers | 409.1 |
| 1007-92 | Performance Requirements for Home Laundry Equipment | 406.1, 406.2 |
| 1008-89 | Performance Requirements for Household Food Waste Disposer Units | 413.1 |
| 1009-90 | Performance Requirements for Commercial Food Waste Grinder Units | 413.1 |
| 1010-82 | Performance Requirements for Water Hammer Arresters – with 1982 Revision | 604.9 |
| 1011-95 | Performance Requirements for Hose Connection Vacuum Breakers | Table 608.1, 608.13.5 |
| 1012-95 | Performance Requirements for Backflow Preventers with Intermediate Atmospheric Vent | Table 608.1, 608.13.3 |
| 1013-95 | Performance Requirements for Reduced Pressure Principle Backflow Preventers | Table 608.1, 608.13.3, 608.16.1 |
| 1014-90 | Performance Requirements for Handheld Showers | 424.3 |
| 1015-93 | Performance Requirements for Double Check Backflow Prevention Assembly – with 1993 Revision | Table 608.1, 608.13.6 |
| 1016-90 | Performance Requirements for Individual Thermostatic, Pressure Balancing and Combination Control Valves for Bathing Facilities | 607.1.1, 607.1.2 |
| 1017-90 | Temperature Actuated Mixing Valves for Primary Domestic Use | 424.4, 607.1.1 |
| 1018-86 | Performance Requirements for Trap Seal Primer Valves. Water Supply Fed – with 1986 Revision | 1002.4 |
| 1019-95 | Performance Requirements for Wall Hydrants, Freezeless, Automatic Draining, Anti-Backflow Types | Table 608.1, 608.13.5 |
| 1020-90 | Performance Requirements for Pressure Vacuum Breaker Assembly | Table 608.1 |
| 1022-96 | Backflow Preventer for Carbonated Beverage Machines | 608.16.1 |
| 1024-94 | Performance Requirements for Dual Check Valve Type Backflow Preventers (for Residential Supply Service or Individual Outlets) | Table 608.1 |
| 1025-78 | Performance Requirements for Diverters for Plumbing Faucets with Hose Spray, Anti-Siphon Type, Residential Applications | 424.2 |
| 1032-80 | Performance Requirements for Dual Check Valve Type Backflow Preventers; for Carbonated Beverage Dispensers – Post Mix-Types | Table 608.1, 608.16.1 |
| 1035-95 | Performance Requirements for Laboratory Faucet Backflow Preventers | Table 608.1, 608.13.5 |
| 1037-90 | Performance Requirements for Pressurized Flushing Devices for Plumbing Fixtures | 425.2 |
| 1044-86 | Performance Requirements for Trap Seal Primer Valves; Drainage Type | 1002.4 |
| 1047-95 | Performance Requirements for Reduced Pressure Detector Assembly Backflow Preventers | Table 608.1 |
| 1048-95 | Performance Requirements for Double Check Detector Assembly Backflow Preventer | Table 608.1, 608.13.6 |
| 1052-94 | Performance Requirements for Hose Connection Backflow Preventers | Table 608.1, 608.13.5 |
| 1056-93 | Back Siphonage Vacuum Breaker | Table 608.1 |
| 5010-1013-1-91 | Field Test Procedure for Reduced Pressure Principle Assembly Using a Differential Pressure Gauge | 312.9 |
| 5010-1015-1-91 | Field Test Procedure for a Double Check Valve Assembly Using a Duplex | 312.9 |
| 5010-1015-2-91 | Field Test Procedure for a Double Check Valve Assembly Using a Differential Pressure Gauge – High- and Low-Pressure Hose Method | 312.9 |
| 5010-1015-3-91 | Field Test Procedure for a Double Check Valve Assembly Using a Differential Pressure Gauge – High-Pressure Hose Method – with August 1992 Revisions | 312.9 |
| 5010-1015-4-91 | Field Test Procedure for a Double Check Valve Assembly Using a Sight Tube | 312.9 |
| 5010-1020-1-91 | Field Test Procedure for a Pressure Vacuum Breaker Assembly | 312.9 |
| 5010-1047-1-91 | Field Test Procedure for a Reduced Pressure Detector Assembly Using A Differential Pressure Gauge | 312.9 |
| 5010-1048-1-91 | Field Test Procedure for a Double Check Detector Assembly Using a Duplex Gauge | 312.9 |
| 5010-1048-2-91 | Field Test Procedure for a Double Check Detector Assembly Using a Differential Pressure Gauge – High- and Low-Pressure Hose Method | 312.9 |
| 5010-1048-3-91 | Field Test Procedure for a Double Check Detector Assembly Using a Differential Pressure Gauge – High-Pressure Hose Method | 312.9 |
| 5010-1048-4-91 | Field Test Procedure for a Double Check Detector Assembly Using a Sight Tube | 312.9 |

| ASTM | American Society for Testing and Materials 100 Barr Harbor Drive West Conshohocken, PA 19428-2959 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| A 53-94 | Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless | Table 605.5, Table 702.1 |
| A 74-94 | Specification for Cast Iron Soil Pipe and Fittings | Table 702.1, Table 702.2, Table 702.3, Table 702.4, 708.2, Table 1102.5 |
| A 377-99 | Standard Index of Specifications for Ductile-Iron Pressure Pipe | 702.1 |
| A 733-89 | Specification for Welded and Seamless Carbon Steel and Austenitic Stainless Steel Pipe Nipples | 605.8 |
| A 888-95 | Specification for Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste and Vent Piping Application | Table 702.1, Table 702.2, Table 702.3, Table 702.4, Table 1102.4, Table 1102.5 |
| B 32-94 | Specification for Solder Metal | 605.14.3, 605.15.4, 705.7.3, 705.8.3 |
| B 42-93 | Specification for Seamless Copper Pipe, Standard Sizes | Table 605.4, Table 702.1 |
| B 43-94 | Specification for Seamless Red Brass Pipe, Standard Sizes | Table 605.4, Table 702.1 |
| B 75-95a | Specification for Seamless Copper Tube | Table 605.4, Table 605.5, Table 702.1, Table 702.2, Table 702.3, Table 1102.4 |
| B 88-93a | Specification for Seamless Copper Water Tube | Table 605.4, Table 605.5, Table 702.1, Table 702.2, Table 702.3, Table 1102.4 |
| B 152-94 | Specification for Copper Sheet, Strip Plate and Rolled Bar | 402.3, 425.3.3, 902.2 |
| B 251-93 | Specification for General Requirements for Wrought Seamless Copper and Copper-Alloy Tube | Table 605.4, Table 605.5, Table 702.1, Table 702.2, Table 702.3, Table 1102.4 |
| B 302-92 | Specification for Threadless Copper Pipe | Table 605.5, Table 702.1 |
| B 306-95a | Specification for Copper Drainage Tube (DWV) | Table 702.1, Table 1102.4 |
| B 447-93 | Specification for Welded Copper Tube | Table 605.4, Table 605.5 |
| B 687-96 | Specification for Brass, Copper, and Chromium-Plated Pipe Nipples | 605.8 |
| B 813-93 | Standard Specification for Liquid and Paste Fixtures for Soldering Applications of Copper and Copper Alloy Tube | 605.14.3, 605.15.4, 705.7.3, 705.8.3 |
| B 828-92 | Practice for Making Capillary Joints by Soldering of Copper and Copper Alloy Tube and Fittings | 605.14.3, 605.15.4, 705.7.3, 705.8.3 |
| C 4-95 | Specification for Clay Drain Tile | Table 702.3, Table 1102.4, Table 1102.5 |
| C 14-95 | Specification for Concrete Sewer, Storm Drain, and Culvert Pipe | Table 702.3, Table 1102.4 |
| C 76-95a | Specification for Reinforced Concrete Culvert, Storm Drain, and Sewer Pipe | Table 702.3, Table 1102.4 |
| C 425-95 | Specification for Compression Joints for Vitrified Clay Pipe and Fittings | 705.13, 705.14 |
| C 428-92 | Specification for Asbestos-Cement Nonpressure Sewer Pipe | Table 1102.4 |
| C 443-94 | Specification for Joints for Circular Concrete Sewer and Culvert Pipe, Using Rubber Gaskets | 705.6, 705.14 |
| C 508-94 | Specification for Asbestos-Cement Underdrain Pipe | Table 1102.5 |
| C 564-95a | Specification for Rubber Gaskets for Cast Iron Soil Pipe and Fittings | 705.5.2, 705.5.3, 705.14 |
| C 700-95 | Specification for Vitrified Clay Pipe, Extra Strength, Standard Strength, and Perforated | Table 702.3, Table 1102.4, Table 1102.5 |
| C 1053-95 | Specification for Borosilicate Glass Pipe and Fittings for Drain, Waste, and Vent (DWV) Applications | Table 702.1, Table 702.4 |
| C 1173-97 | Specifications for Flexible Transition Couplings for Underground Piping Systems | 705.6, 705.12.1, 705.13, 705.14 |
| C 1277-98 | Standard Specification for Shielded Couplings Joining Hubless Cast-iron Soil Pipe and Fittings | 705.5.3 |
| D 1869-95 | Specification for Rubber Rings for Asbestos-Cement Pipe | 705.14 |
| D 2564-93 | Specification for Solvent Cements for Poly (Vinyl Chloride) (PVC) Plastic Pipe and Fittings | 705.12.2 |
| D 2661-96 | Specification for Acrylonitrile-Butadiene-Styrene (ABS) Schedule 40 Plastic Drain, Waste, and Vent Pipe and Fittings | Table 1102.4 |
| D 2665-96 | Specification for Poly (Vinyl Chloride) (PVC) Plastic Drain, Waste, and Vent Pipe and Fittings | Table 702.1, Table 702.3, Table 1102.4 |
| D 2729-96 | Specification for Poly (Vinyl Chloride) (PVC) Sewer Pipe and Fittings | Table 1102.4, 1102.5 |
| D 2751-96 | Specification for Acrylonitrile-Butadiene-Styrene (ABS) Sewer Pipe and Fittings | Table 1102.4 |
| D 2846-96 | Specification for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Hot and Cold Water Distribution Systems | Table 605.4, 605.16.2 |
| D 2855-96 | Standard Practice for Making Solvent-Cemented Joints with Poly (Vinyl Chloride) (PVC) Pipe and Fittings | 705.12.2 |
| D 2949-96 | Specification for 3.25-in Outside Diameter Poly (Vinyl Chloride) (PVC) Plastic Drain, Waste, and Vent Pipe and Fittings | Table 702.1 |
| D 3034-96 | Specification for Type PSM Poly (Vinyl Chloride) (PVC) Sewer Pipe and Fittings | Table 1102.4 |
| D 3212-96 | Specification for Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals | 705.12.1 |
| D 3311-94 | Specification for Drain, Waste and Vend (DWV) Plastic Fittings Patterns | Table 702.4 |
| D 4551-96 | Specification for Poly (Vinyl Chloride) (PVC) Plastic Flexible Concealed Water-Containment Membrane | 417.5 |
| F 437-96 | Specification for Threaded Chlorinated Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80 | Table 605.6 |
| F 438-93 | Specification for Socket-Type Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe Fittings, Schedule 40 | Table 605.6 |
| F 439-93a | Specification for Socket-Type Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe Fittings, Schedule 80 | Table 605.6 |
| F 441-94 | Specification for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe, Schedules 40 and 80 | Table 605.5 |
| F 442-94 | Specification for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe (SDR- PR) | Table 605.5 |
| F 477-96 | Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe | 705.14 |
| F 493-93a | Specification for Solvent Cements for Chlorinated Poly (Vinyl Chloride) (CPVC) Plastic Pipe and Fittings | 605.16.2 |
| F 628-96 | Specification for Acrylonitrile-Butadiene-Styrene (ABS) Schedule 40 Plastic Drain, Waste and Vent Pipe with Cellular Core | Table 1102.4 |
| F 656-96 | Specification for Primers for Use in Solvent Cement Joints of Poly (Vinyl Chloride) (PVC) Plastic Pipe and Fittings | 705.12.2 |
| F 891-96 | Specification for Coextruded Poly (Vinyl Chloride) (PVC) Plastic Pipe with a Cellular Core | Table 1102.4, Table 1102.5 |
| F 1412-99 | Specification for Polyolefin Pipe and Fittings for Corrosive Waste Drainage Systems | 605.5, 605.6, 702.1 |

| AWS | American Welding Society 550 N.W. LeJeune Road P.O. Box 351040 Miami, FL 33135 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| A5.8-92 | Specifications for Filler Metals for Brazing | 605.12.1, 605.14.1, 605.15.1, 705.4.1, 705.7.1, 705.8.1 |

| AWWA | American Water Works Association 6666 West Quincy Avenue Denver, CO 80235 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| C 104-95 | Cementmortar Lining for Ductileiron Pipe and Fittings for Water | 605.4, 605.6 |
| C 110-93 | Standard for Ductile-Iron and Gray-Iron Fittings, 3 Inch through 48 Inches, for Water and Other Liquids | Table 605.6, Table 702.4 |
| C 111-95 | Rubber Gasket Joints for Ductile Iron Pressure Pipe and Fittings | 605.13 |
| C 115-99 | Flanged Ductile-Iron Pipe with Ductile-Iron or Gray-Iron Threaded Flanges | 702.1, 702.2 |
| C 151-91 | Standard for Ductile-Iron Pipe, Centrifugally Cast for Water or Other Liquids | Table 605.4, 702.1, 702.2 |
| C 153-00 | Ductile-Iron Compact Fittings for Water Service | Table 605.6 |
| C 510-95 | Double Check Valve Backflow-Prevention Assembly | 608.13.6 |
| C 511-92 | Reduced-Pressure Principle Backflow-Prevention Assembly | 608.13.2 |

| CABO | Council of American Building Officials Suite 201 5203 Leesburg Pike Falls Church, VA 22041 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| A117.1-92 | Accessible and Usable Building and Facilities | 401.1, 404.1 |

| CSA | Canadian Standards Association 178 Rexdale Blvd. Rexdale (Toronto), Ontario, Canada M9W IR3 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| A257.1-92 | Circular Concrete Culvert, Storm Drain, Sewer Pipe and Fittings | Table 702.3, Table 1102.4 |
| A257.3-92 | Joints for Circular Concrete Sewer and Culvert Pipe, Manhole Sections, and Fittings Using Rubber Gaskets | 705.6, 705.14 |
| B45.1-94 | Ceramic Plumbing Fixtures | 408.1, 416.1, 418.1, 419.1, 420.1, 421.1 |
| B45.2-94 | Enameled Cast-Iron Plumbing Fixtures | 407.1, 415.1, 416.1, 418.1 |
| B45.3-94 | Porcelain Enameled Steel Plumbing Fixtures | 407.1, 416.1, 418.1 |
| B45.4-94 | Stainless-Steel Plumbing Fixtures | 415.1, 416.1, 418.1, 420.1 |
| B45.5-94 | Plastic Plumbing Fixtures | 407.1, 416.2, 417.1, 419.1, 420.1, 421.1 |
| B64.7-94 | Vacuum Breakers, Laboratory Faucet Type (LFVB) | Table 608.1 |
| B64.10-94 | Manual for the Selection, Installation, Maintenance and Field Testing of Backflow Prevention Devices | 312.9 |
| B79-79 | Floor, Area and Shower Drains, and Cleanouts for Residential Construction | 412.1 |
| B137.6-83 | CPVC Pipe, Tubing and Fittings for Hot and Cold Water Distribution Systems | Table 605.5 |
| B181.1-96 | ABS Drain, Waste, and Vent Pipe and Pipe Fitting | Table 702.1 |
| B182.2-95 | PVC Sewer Pipe and Fittings (PSM Type) | Table 702.3, Table 1102.4, Table 1102.5 |
| CAN/CSA-A257.2-92 | Reinforced L Circular Concrete Culvert, Storm Drain, Sewer Pipe and Fittings | Table 702.3, Table 1102.4 |
| CAN/CSA-B64.1.1-94 | Vacuum Breakers, Atmoshperic Type (AVB) | 425.2, Table 608.1, 608.13.5 |
| CAN/CSA-B64.2-94 | Vacuum Breakers, Hose Connection Type (HCVB) | Table 608.1, 608.13.5 |
| CAN/CSA-B64.2.2-94 | Vacuum Breakers, Hose Connection Type (HCVB) with Automatic Draining Feature | Table 608.1, 608.13.5 |
| CAN/CSA-B64.3-94 | Backflow Preventers, Dual Check Valve Type with Atmospheric Port (DCAP) | Table 608.1, 608.13.3 |
| CAN/CSA-B64.4-94 | Backflow Preventers, Reduced Pressure Principle Type (RP) | Table 608.1, 608.13.2 |
| CAN/CSA-B125-94 | Plumbing Fittings | 424.1, 424.2, 424.3, 424.4, 425.3.1, 425.4, Table 608.1 |
| CAN/CSA-B137.3-93 | Rigid Poly (Vinyl Chloride) (PVC) Pipe for Pressure Applications | 705.12.2 |
| CAN/CSA-B181.1-96 | ABS Drain, Waste, and Vent Pipe and Pipe Fittings | 715.3 |
| CAN/CSA-B181.2-90 | PVC Drain, Waste, and Vent Pipe and Pipe Fittings | Table 702.1, 705.12.2, 715.3 |
| CAN/CSA-B182.1-92 | Plastic Drain and Sewer Pipe and Pipe Fittings | 705.12.2 |
| CAN/CSA-B182.2-83 | PVC Sewer Pipe and Fittings (PSM Type) | 1102.5 |
| CAN/CSA-B182.4-92 | Profile PVC Sewer Pipe and Fittings | Table 1102.4, Table 1102.5 |
| CAN/CSA-B602-90 | Mechanical Couplings for Drain, Waste, and Vent Pipe and Sewer Pipe | 705.5.3, 705.6, 705.12.1, 705.13, 705.14 |
| CSA-B45-88 | (Supplement 1) – Hydromassage Bathtubs | 421.1 |

| CISPI | Cast Iron Soil Pipe Institute Suite 419 5959 Shallowford Road Chattanooga, TN 37421 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| 301-95 | Specification for Hubless Cast Iron Soil Pipe and Fittings for Sanitary and Storm Drain, Waste and Vent Piping Applications | Table 702.1, Table 702.2, Table 702.3, Table 702.4, Table 1102.4, Table 1102.5 |
| 310-95 | Specification for Coupling for Use in Connection with Cast-Iron Soil Pipe and Fittings for Sanitary and Storm Drain Waste and Vent Piping Applications | 705.5.3 |

| FS | Federal Specification General Service Administration 7th & D Streets Specification Section, Room 6039 Washington, DC 20407 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| TT-P-1536a-75 | Federal Specification for Plumbing Fixture Setting Compound | 405.4 |

| NFPA | National Fire Protection Association Batterymarch Park Quincy, MA 02269 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| 70-93 | National Electrical Code | 502.1, 1111.3.3 |

| NSF | National Sanitation Foundation 3475 Plymouth Road P.O. Box 130140 Ann Arbor, MI 48113-0140 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| 14-90 | Plastic Piping Components and Related Materials | 303.3 |
| 42-88 | Drinking Water Treatment Units – Aesthetic Effects | 611.1 |
| 53-96 | Drinking Water Treatment Units – Health Effects | 611.1 |
| 58-96 | Reverse Osmosis Drinking Water Treatment Systems | 611.2 |
| 61-95 | Drinking Water System Components – Health Effects | 605.4, 605.5, 605.6 |

| PDI | Plumbing and Drainage Institute 1106 West 77th Street, South Drive Indianapolis, IN 46260-3318 |  |
| --- | --- | --- |
| Standard Reference Number | Title | Referenced in code section number |
| G101-85 | Testing and Rating Procedure for Grease Interceptors with Appendix of Sizing and Installation Data | 1003.3 |

- Appendix A
Procedures for Calculating the Minimum Sizing of the Water Supply System

For a printer-friendly PDF version of Appendix A, please click here.

The following is a procedure that shall be used in calculating the minimum sizing of the water supply system:

Step 1.      Compute the total number of fixture units from Table 18-29-604.10.1, Demand Weight of Fixtures in Fixture Units.

1.     For supply outlets likely to impose continuous demands, estimate continuous supply separately and add to total demand for fixtures.

2.     For fixtures not listed, weights may be assumed by comparing the fixture to a listed one using water in similar quantities and at similar rates.

3.     The given weights are for total demand. For fixtures with both hot and cold water supplies, the weights for maximum separate demand may be taken as three-fourths the listed demand for supply.

Table 18-29-604.10.1
Demand Weight of Fixtures in Fixture Units

Fixture Type; Occupancy Use; Valve Type; Fixture Units. Water Closet; Public; Flush Valve; 10. Water Closet; Public; Flush Tank; 5. Urinal 1"; Public; Flush valve; 10. Urinal 3/4"; Public; Flush valve; 5. Urinal Tank; Public; Flush tank; 3. Lavatory; Public; Faucet; 2. Bathtub; Public; Faucet; 4. Shower head; Public; Mixing valve; 4. Service sink; Office, etc.; Faucet; 3. Kitchen sink; Hotel or restaurant; Faucet; 4. Water closet; Private; Flush valve; 6. Water closet; Private; Flush tank; 3. Lavatory; Private; Faucet; 1. Bathtub; Private; Faucet; 2. Shower head; Private; Mixing valve; 2. Bathroom group; Private; Flush valve for closet; 8. Bathroom group; Private; Flush tank for closet; 4. Separate shower 109; Private; Mixing valve; 2. Kitchen sink; Private; Faucet; 2. Laundry trays (1 to 3); Private; Faucet; 2. Combination fixture; Private; Faucet; 3. Laundry washer; Private; Faucet; 2. Bidet; Private; Faucet; 2. Dishwasher; –; –; 2. Drinking fountain; –; –; 1/2. Laundry washer; Public; 8 lbs; 3. Laundry washer; Public; 15 lbs; 4. Water closet; Public/Private; Flushometer tank; 2.

Step 2.     Using Table 18-29-604.10.2, convert the total water demand from fixture units to gallons per minutes (gpm). Add any continuous supply demand in gpm such as lawn sprinklers, air conditioning, industrial uses, etc., to the sum of the total demand for fixtures. The result is the total required gpm demand. All distributing pipes, riser pipes and branch distributing pipes shall be sized in accordance with the demand indicated in Table 18-29-604.10.2 of this chapter.

Beyond the capacity listed in Table 18-29-604.10.2, the service pipe, main supply pipe, principal supply pipe and the branch supply pipe shall be sized to meet the velocity of water flow provisions of this chapter. Data shall be provided by the designer to substantiate this.

Table 18-29-604.10.2 – Part 1
Conversion of Total Water Demand

For Systems Predominantly Flush Tanks; For Systems Predominantly for Flush Valves. Load; Demand; Load; Demand. 1; 1.5; 1; –. 2; 2.5; 2; –. 3; 3.3; 3; –. 4; 4.0; 4; –. 5; 4.8; 5; 15.0. 6; 5.5; 6; 17.5. 7; 5.7; 7; 19.7. 8; 6.9; 8; 22.2. 9; 7.5; 9; 24.5. 10; 8.2; 10; 27.0. 11; 8.8; 11; 27.8. 12; 9.5; 12; 28.5. 13; 10.1; 13; 29.5. 14; 10.8; 14; 30.1. 15; 11.4; 15; 31.0. 16; 12.0; 16; 31.8. 17; 12.5; 17; 32.6. 18; 13.0; 18; 33.5. 19; 13.5; 19; 34.2. 20; 14.2; 20; 35.0. 25; 17.0; 25; 38.2. 30; 19.4; 30; 41.5. 35; 21.8; 35; 43.6. 40; 24.3; 40; 46.0. 45; 26.8; 45; 48.2. 50; 29.0; 50; 50.5.

Table 18-29-604.10.2 – Part 2
Demand Weight of Fixtures

For Systems Predominantly for Flush Tanks; For Systems Predominantly for Flush Valves. Load W.S.F.U.; Demand GPM; Load W.S.F.U.; Demand GPM. 60; 32.0; 60; 54.6. 70; 35.0; 70; 58.7. 80; 38.0; 80; 61.5. 90; 41.0; 90; 65.0. 100; 44.0; 100; 68.0. 120; 48.0; 120; 74.0. 140; 53.0; 140; 78.0. 160; 57.0; 160; 82.0. 180; 61.0; 180; 86.0. 200; 65.0; 200; 90.0. 225; 70.0; 225; 95.0. 250; 75.0; 250; 100.0. 275; 80.0; 275; 102.0. 300; 85.0; 300; 106.0. 400; 105.0; 400; 125.0. 500; 124.0; 500; 142.0. 750; 170.0; 750; 176.0. 1000; 208.0; 1000; 208.0. 1250; 237.0; 1250; 237.0. 1500; 262.0; 1500; 262.0. 1750; 283.0; 1750; 283.0. 2000; 302.0; 2000; 302.0. 2500; 337.0; 2500; 337.0. 3000; 362.0; 3000; 362.0. 3500; 387.0; 3500; 387.0. 4000; 412.0; 4000; 412.0.

Step 3.     Determine the elevation of the highest fixture or group of fixtures or water opening above the city water main or other source of pressure supply. Multiply this elevation in feet by 0.434. The result is the loss in static pressure in pounds per square inch (psi).

Step 4.     Compute the size of meter necessary for a total water demand.

Step 5.     Compute the pressure loss through the meter. For pressure losses, consult manufacturer's data.

Step 6.     Compute the available pressure to overcome friction in the piping system. First compute all losses (see below):

1)     Subtract the above losses from the minimum service pressure in the water main or other source of supply. The remaining is the available pressure to overcome friction within an upfeed piping system.

2)     For gravity water tanks, determine the vertical distance between the incoming water service, the minimum tank water line, and the highest fixture or group of fixtures or water opening. To find the available pressure to overcome friction in the downfeed piping system, multiply the distance defined above by 0.434, then subtract the above losses from this pressure. The remaining is the available pressure to overcome friction within the downfeed piping system.

Step 7.     Compute the developed length of the basic circuit of piping from the main in the street, the house pump, the outlet side of the pressure-reducing valve or other source of supply pressure to the highest and farthest outlet.

For a gravity water tank, compute the developed length of the basic circuit of the piping from the tank connection to the highest and most remote outlet. Developed length plus 50 percent will approximate the equivalent length run (ELR).

Step 8.     Compute the pressure factor per 100 feet of developed length. From the above calculations, take the pressure available for friction loss in psi, (Step 6) divide by the equivalent length run (ELR) (Step 7) and multiply by 100 to ascertain the maximum uniform pressure loss for friction in the piping of the basic circuit. (See Table 18-29-604.10.3)

Step 9.     Knowing the permissible uniform friction loss per 100 feet of pipe and the fixture gpm and all continuous demands in gpm, the diameter of the building service and main supply pipe to the cold and hot water branch or the first branch may be obtained from Table 18-29-604.10.2.

The diameter of pipe on the coordinate point corresponding to the estimated demand and the permissible uniform friction loss shall be the size of the service and main supply pipe to cold and hot water branch or the first branch.

All other piping in the water supply system shall be sized according to the full-listed demand weight, with the exception of piping that supplies fixtures with both cold and hot water, which may be sized at three-fourths of the listed demand weight for cold or hot water piping. All continuous demands on the piping system shall be included in the fixture gpm demand.

For fixtures not listed, demand weights may be assumed by comparing the fixture to a listed one using water in similar quantities and at similar rates.

The cold and hot water principal supply pipe, branches and risers may be obtained from either Table 18-29-604.10.3 or 18-29-604.10.4, whichever is applicable. The diameter of pipe on or directly above the coordinate point corresponding to the estimates* demand and the permissible uniform friction loss shall be the size of the pipe.

* Editor's note – As set forth in Coun. J. 3-28-01, p. 55444, § 1; correct language appears to be “estimated”.

No service shall be less than 1 inch nominal pipe size. Where 1 inch flushometer valves are used, the minimum size of water service shall be a 1 1/2 inch nominal pipe size and the minimum size of the riser shall be a 1 1/4 inch nominal pipe size. No riser shall be less than 3/4 inch nominal pipe size.

Table 18-29-604.10.3
Allowance in Equivalent Length of Pipe for Friction Loss in Valves and Threaded Fittings

Diameter of Fitting (Inches); 90-DEG Standard ELL (Feet); 45-DEG Standard ELL (Feet); 90-DEG Side Tee (Feet); Coupling or Straight Run of Tee (Feet); Gate Valve (Feet); Globe Valve (Feet); Angle Valve (feet). 3/8; 1; 0.6; 1.5; 0.3; 0.2; 8; 4. 1/2; 2; 1.2; 3; 0.6; 0.4; 15; 8. 3/4; 2.5; 1.5; 4; 0.8; 0.5; 20; 12. 1; 3; 1.8; 5; 0.9; 0.6; 25; 15. 1 1/4; 4; 2.4; 6; 1.2; 0.8; 35; 18. 1 1/2; 5; 3; 7; 1.5; 1.0; 45; 22. 2; 7; 4; 10; 2; 1.3; 55; 28. 2 1/2; 8; 5; 12; 2.5; 1.6; 65; 34. 3; 10; 6; 15; 3; 2; 80; 40. 3 1/2; 12; 7; 18; 3.6; 2.4; 100; 50. 4; 14; 8; 21; 4.0; 2.7; 125; 55. 5; 17; 10; 25; 5; 3.3; 140; 70. 6; 20; 12; 30; 6; 4; 165; 80.

(Amend Coun. J. 3-27-02, p. 82090, § 3)