MECHANICAL DESIGN MANUAL SUMMARY SHEET

SUBJECT:		Domestic Hot Water Recirculation

DESCRIPTION:	Design guidelines for designing and sizing hot water recirculation systems

SPEC SECTION:	15410

REFERENCES:	1989 ASPE Data Book, Chapter 4 Service Hot Water Systems

ASPE Domestic Water Heating Design Manual

Plumbing Engineer Magazine, September 1997, Prompt Delivery of Hot Water at Fixtures, by Edward Saltzberg, P.E., CEM, CIPE

ASHRAE 1999 Applications Handbook, Chapter 48 Service Water Heating

DATE:		March 2000

PREPARED BY:	Plumbing Committee (Russ Meier/John Karben)

DOMESTIC HOT WATER RECIRCULATION

Energy in the form of heat is always being transferred from domestic hot water to its surroundings. Insulating the piping only increases the duration of time required for the water to reach ambient temperature.  Unless energy is added to the water to offset losses, the water temperature will drop below acceptable levels.

Recirculation of domestic hot water through the water heater provides the heat required to offset piping heat losses.  Both water conservation and user satisfaction results from maintaining a consistent water temperature.  Proper recirculation eliminates excessive delays in obtaining hot water at a plumbing fixture and minimizes the volume of unused water discharged down the drain.

Recirculation of domestic hot water may also provide health benefits.  Stagnant water in the domestic water piping can provide ideal growth zones for some microbial organisms.  The lower temperatures due to heat loss and the scaling due to stagnant water are commonly blamed for an increased microbial growth in uncirculated domestic hot water piping and dead legs.

The first cost of a recirculation system includes the pump, recirculation piping, insulation, balancing valves, check valves and isolation valves. Balancing costs will also be incurred to ensure satisfactory performance of the hot water recirculation system.

# DESIGN CRITERIA

Each of the following issues must be addressed for a complete recirculation system:

- Heat loss rate from distribution piping.

- Allowable temperature drop.

- Flow rate

- Piping arrangement to minimize distance to fixtures.

- Pump selection.

## Heat Loss Rate

The entire hot water distribution system from the source to each fixture must be considered for calculating the systems heat loss rate. Hot water recirculation piping can be disregarded in most cases unless there is a concern for microbial growth and the recirculation system reaches temperatures below 120 °F.

Heat loss from insulated pipe can be calculated using the following equation. The accompanying spreadsheet will aid in system takeoff and heat loss calculation.

| Q = x A | where: Q = BTU per hour per lineal foot of pipe A = Square feet of pipe insulation surface per lineal foot of pipe q = BTU per hour per square foot of outer surface of insulation |
| --- | --- |
|  | where: r1 = inner radius of insulation in inches r2 = outer radius of insulation in inches t1 = temperature, inner surface of insulation t2 = temperature, ambient k = thermal conductivity at mean temperature Rs = air film resistance Ln = natural logarithm |

## Allowable Temperature Drop

Each system must be evaluated for the allowed temperature drop from the hot water source to the most remote fixture. The difference of temperature between the source and the minimum required at the fixture will govern the allowable temperature drop. There can be multiple allowable temperature drops for different branch segments on a single system. Following are suggested system temperatures:

Hot Water Source: 140 °F recommended to 120 °F minimum.

Plumbing Fixtures:

Lavatories: 		105-115 °F

Sinks:		115-130 °F	depending on usage (lower temps for mainly hand washing, higher temps if handling dishes)

Mop Basins:	130 °F

Kitchen Equip.	130-180 °F	Refer to kitchen equipment consultant and/or codes.

Shower Valves	130-135 °F	This is hot water supply temp to the mixing valve not the discharge temperature. Mixing valves work most accurately with a greater temperature between the cold and hot water.

Example: If a systems hot water source is set at 140 °F a branch serving just lavatories could have a allowable temperature drop of 25-35 °F where a branch line serving showers would only have a 5-10 °F drop.

The greater the temperature drop allowed the lesser the flow rate required and therefore less pumping energy consumed. But the lower the temperature the greater risk of microbial growth. Most designs should not allow the temperature to drop below 120 °F on any part of the distribution piping. The recommend allowable temperature drop is between 2 and 10 °F.

## Flow Rate

With the known heat loss rate and allowable temperature drop the system flow rate can be established to offset the heat loss. Flow rate can be calculated using the following equation. The accompanying spreadsheet will aid in calculating flow rates for each of the system’s branch segments.

M=QTotal60minhr⋅ρ⋅cp⋅ΔTs≈QTotal500⋅ΔTs

where:

M  = Flow rate of water required to offset heat loss (GPM)

Q  = Summation of all heat loss in supply and return piping (BTU/h)

ρ = Density of water ( 8.33 lb/gal )

cp = Specific heat of water ( 1 BTU/lbF)

ΔTs = Allowable temperature drop in system supply water temperature (F)

Install a balancing valve on each branch segment to maintain proper flow.

## Piping Arrangement

The building’s hot water system consists mainly of four components. Starting from the source they are: the hot water main, hot water branch, recirculation branch (branch segments) and recirculation main (longest segment). Fixture rough-in piping is the final component that distributes the hot water from the main or branch to the fixture. To properly distribute hot water a main or branch must be within a given distance to a fixture to satisfy occupants and conserve water.

The following table describes the time it takes for hot water to reach a fixture from distances of 10 and 25 feet at listed gpm flow rates.

| APPROXIMATE TIME REQUIRED TO GET HOT WATER TO A FIXTURE |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DELIVERY TIME (SECONDS) |  |  |  |  |  |  |  |  |  |
| FIXTURE FLOW RATE |  | 0.5 (GPM) |  | 1.5 (GPM) |  | 2.5 (GPM) |  | 4 (GPM) |  |
| MATERIAL | PIPE SIZE | 10 ft | 25 ft | 10 ft | 25 ft | 10 ft | 25 ft | 10 ft | 25 ft |
| Copper pipe | 1/2" | 25 | 63 | 8 | 21 | 5 | 13 | 3 | 8 |
|  | 3/4" | 48 | 119 | 16 | 40 | 10 | 24 | 6 | 15 |
| Steel Pipe schedule 40 | 1/2" | 63 | 157 | 21 | 52 | 13 | 31 | 8 | 20 |
|  | 3/4" | 91 | 228 | 30 | 76 | 18 | 46 | 11 | 28 |
| CPVC Pipe schedule 40 | 1/2" | 64 | 159 | 21 | 53 | 13 | 32 | 8 | 20 |
|  | 3/4" | 95 | 238 | 32 | 79 | 19 | 48 | 12 | 30 |

Note:

Calculations are based on the amount of heat required to heat the piping, the water in the piping, and the heat loss from the piping.

This table describes how far a fixture can be from a circulated main and receive hot water at a given time interval and fixture rough-in pipe size.

| APPROXIMATE DISTANCE FROM CIRCULATED MAIN TO FIXTURE (FEET) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DELIVERY TIME (SECONDS) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FIXTURE FLOW RATE |  | 0.5 (GPM) |  |  | 1.5 (GPM) |  |  | 2.5 (GPM) |  |  | 4 (GPM) |  |  |
| Material | PIPE SIZE | 10 SEC | 20 SEC | 30 SEC | 10 SEC | 20 SEC | 30 SEC | 10 SEC | 20 SEC | 30 SEC | 10 SEC | 20 SEC | 30 SEC |
| Copper pipe | 1/2" | 6.9 | 13.9 | 20.8 | 20.8 | 41.7 | 62.5 |  |  |  |  |  |  |
|  | 3/4" | 3.3 | 6.7 | 10 | 10 | 20 | 30 | 16.7 | 33.3 | 50 | 26.6 | 53.3 | 80 |
|  | 1" | 1.9 | 3.9 | 5.8 | 5.8 | 11.6 | 17.4 | 9.7 | 19.4 | 29 | 15.5 | 31 | 46.5 |

Notes:

This assumes replacing 100% of the ambient temperture water from the fixture rough-in piping and does not include any losses for heating up piping and insulation.

Delays of zero to ten seconds are typically considered acceptable for residential or public fixtures. Delays between 11 to 30 seconds are considered marginal but usually acceptable. Delays beyond 31 seconds are considered unacceptable. (ASPE Domestic Water Heating Manual pg. 198)

ADA sets a minimum time of 15 seconds for a fixture to discharge water at design temperature. Unless hot water reaches the fixture in less than 15 seconds, ADA considers adequate hot water unavailable.

Low flow fixtures (lavatories) can take considerably longer to obtain hot water. The Energy Conservation Act of 1993 mandates the use of low flow faucets for lavatories in public areas, therefore to minimize delays lavatories shall not be more than 10 feet and sinks and showers shall not be more than 20 feet from a circulated hot water pipe unless the fixture or group of fixtures will operate to Owner and “Authority Having Jurisdiction” satisfaction. If at all possible keep the delay to obtain hot water to under 10 seconds.

When sizing hot water recirculation piping there are maximum velocities not to exceed. Velocities maintained above these values can result in leaks in less than six months. See the chart below for maximum gpm for a given pipe size. One inch pipe and under should not exceed three feet per second velocities.

| MAXIMUM RECOMMENDED FLOW RATE AND PRESSURE DROP FOR HOT WATER AND HOT WATER RECIRCULATION PIPING |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | COPPER PIPE SIZES |  |  |  |  |  |  |
|  | 1/2" | 3/4" | 1" | 1-1/4" | 1-1/2" | 2" | 2-1/2" |
| 3 FPS | 2 GPM | 5 GPM | 8 GPM | 12 GPM | 17 GPM | 30 GPM | 50 GPM |
|  | 10' / 100' | 8' /100' | 4.5 '/100' | 3.75' /100' | 3' /100' | 2' /100' | 2' /100' |
| 4 FPS |  |  |  | 16 GPM | 22 GPM | 40 GPM | 60 GPM |
|  |  |  |  | 6' /100' | 5' /100' | 3.5' /100' | 2.75' /100' |

## Pump Selection

Circulating pumps are typically small in-line pumps. Installation should include isolation valves, a check valve and P/T plugs.

Pump selection is based on total gpm for the system and a pump head calculation for the most remote branch on the system. Mixing valves have approximate 10 psi (23 feet) of pressure drop through them. Make sure to include them in pump head calculation. Refer to manufacturer literature for exact pressure drops.

If a system has two or more different temperature distribution systems from a single source (i.e. 180 °F and 140 °F) provide separate recirculation pumps for each system.

Control of the recirculation pump can be manual, by a thermostatic aquastat or by time clock based on building occupancy.

# DESIGN TAKE-OFF/SIZING PROCEDURE

Refer to the attached Hot Water Recirculation Spreadsheet Instructions page.

# ALTERNATE SYSTEMS TO CONSIDER

Point-of-use heaters: Eliminates hot water and recirculation mains and branch piping. Installation cost may be higher along with additional maintenance costs.

Heat Trace: Eliminates recirculation mains and branch piping. Allows for stagnant water, which promotes microbial growth. Potential higher operating costs. Refer to manufacturer’s literature for design information.

# DESIGN CONSIDERATIONS

- Copper pipe is preferred over galvanized piping for domestic hot water service.

- Legionella multiplies at a much faster rate when temperatures are between 88 and 120°F.

- Hot water piping sized with velocities below 2 feet per second does not carry entrained air.

- Provide a balancing valve, check valve and isolation valve where the recirculation branch segment connects to the recirculation main. The check valve will prevent recirculation water from being drawn back to the fixture.

- Install air vents at high points in piping systems.

- Renovation projects may have higher piping heat losses due to piping with no insulation or portions of piping where insulation has fallen off the pipe. Higher safety factors should be used. If feasible all piping should be reinsulated.

- Lay out hot water piping to minimize piping.  Point-of-use water heaters or electric heat trace may better serve individual fixtures on long branches. Capitol Development Board (CDB) projects must have prior approval to use heat tracing.

- Heat trace can be used in conjunction with recirculation systems.

- Protect insulation from water since wet insulation actually increases heat transfer.

- Pressure drop through water heaters, storage tanks, balancing valves, mixing valves, isolation valves, check valves and piping should all be included in recirculation pump head calculations.

- An aquastat can be used to cycle recirculation pumps as required to maintain an acceptable water temperature range.

- Energy codes or owners (ASHRAE 90.1) may require timers to turn recirculation pumps off during night time or other periods when the building is unoccupied or has low probability of demand.

- Recirculation pumps shall be constructed of corrosion resistant materials, typically bronze.

Hot Water Recirculation Spreadsheet Instructions

p:\mech\spreadsheets\hwc.xlt

Page 1: Summary Sheet

- Fill in Name, Date, Engineer Name and Project Number.

- Review Design Parameters. Adjust per job specifics.

- Review Insulation thicknesses and adjust per job specifics. KJWW standard spec thicknesses are listed. (Note: Info is outside of standard print range)

All other information is automatically filled in from input on pages 2 through 5

Page 2: Pump Head

Standard pump head calculation based on longest run including return piping to heater.

- Pump GPM is equal to the sum off all Branch Segments and Longest Segment.

Pages 3 - 5: Worksheets

- Starting with the Longest Segment table, input lengths for each size of pipe from the heater to the furthest hot water line in the system. Include return piping back to the heater if desired/necessary.

- Next go to Branch Segment #1 table; move up your system from the heater to the first branch line. Take off lengths for each size of pipe from the hot water main to the last fixture served on the branch. Include return piping if desired/necessary.

- Continue up the system taking off all the Branch Segments in the same manner.

- Input the allowed temperature drop for each of the branch segments. The supply temperature for each of the branch segments will be between the heater setpoint and the minimum temperature (see settings on Page 1). To maintain the systems minimum temperature the Branch Segment=s allowed temperature drop must be reduced the further you go out in the system.

Example: A system with a 140 deg setting at the heater and minimum temperature of 135 deg (5 deg temperature drop) a Branch Segment near the heater would have a maximum temperature drop of 4 deg where a Branch Segment near the end of the system would have a maximum temperature drop of 1 to 2 degrees.

# On the drawings

- Provide a shutoff valve, check valve and balancing valve at each Branch Segments=s and Longest Segment=s return pipe where it connects to the main return pipe.

- Label the balancing valve with the GPM setpoint based on the spreadsheet.